## Base
| Parameters | Data
Base data | Location Name | Bangalore
| Latitude | 12.966
| Longitude | -77.35
| Target Capacity (MWp) | 1
| Plant Life | 25
| Tilt angle | 12.966
| Surface azimuth | 0
Module | Manufacturer | Tata Power Solar
| Technology | Multi Crystalline
| Model | TS250
| Module Power (Wp) | 250
| Voc STC (V) | 38.1
| Isc STC (A) | 8.58
| Vmp STC (V) | 30.7
| Imp STC (A) | 8.16
| Length (m) | 1
| Breadth (m) | 1.667
| Temp Coeff of Pmax (%/C) | -0.4383
| Temp Coeff of Voc (%/C) | -0.3305
| Temp Coeff of Isc (%/C) | 0.0638
| Module Rating at end of year 1 (%) | 97%
| Year on Year degradation rate (%/year) | -0.6667%
PCU | Manufacturer | Eaton
| Model | Power Xpert
| Efficiency (%) | 96%
| AC Power (kVA) | 250
| Nominal DC Power (kW) | 250
| Vmpp min (V) | 300
| Vmpp max (V) | 500
| Vstart (V) | 400
| V DC max (V) | 600
| I nom DC (A) | 860
| I max DC (A) | 1340
Mount | Module Type | Glass/Cell/Polymer Sheet
| Mount Style | Open Rack
| Mount: a | -3.56
| Mount: b | -0.075
| Mount: ΔT | 3
Misc | Albedo | 0.2
| Array Height (m) 1.25 to 1.5 | 1.5
| Ground Clearance (m) | 0.5
| Boundary Spacing along length - a (m) | 10
| Boundary Spacing along breadth - b (m) | 10
| Soiling Loss (%) | 5%
| Electrical Loss (%) | 8%
| Rate for Aux Consumption of yr 1 (%) | 1%
Note on B3: Author: N + , S -
Note on B4: Author: E - , W +

## Solar Data
Hour | GHI | DHI | DNI | Tamb | WS
0 | 0 | 0 | 0 | 16.2 | 0.28
1 | 0 | 0 | 0 | 15.5 | 2.78
2 | 0 | 0 | 0 | 14.9 | 2.78
3 | 0 | 0 | 0 | 14.2 | 3.33
4 | 0 | 0 | 0 | 13.7 | 3.89
5 | 0 | 0 | 0 | 13.2 | 1.94
6 | 8.3 | 5.6 | 9.9 | 14.1 | 2.78
7 | 88.9 | 77.8 | 43.5 | 15.4 | 3.89
8 | 451.4 | 135.7 | 641.5 | 16.6 | 5.56
9 | 665 | 166.9 | 752.8 | 17.9 | 5
10 | 824.6 | 197 | 806.5 | 19.4 | 5.56
11 | 925 | 152.8 | 963.4 | 22 | 5
12 | 919.4 | 144.4 | 966.8 | 23.5 | 5
13 | 847.2 | 152.8 | 937.2 | 23.9 | 5
14 | 708.3 | 155.6 | 886 | 24.1 | 4.44
15 | 496.9 | 136.1 | 764 | 23.5 | 5.56
16 | 283.3 | 105.6 | 692.3 | 22.2 | 5
17 | 30.6 | 11.1 | 9.9 | 21.4 | 4.44
18 | 0 | 0 | 0 | 19.7 | 4.44
19 | 0 | 0 | 0 | 18.6 | 3.89
20 | 0 | 0 | 0 | 17.6 | 3.33
21 | 0 | 0 | 0 | 16.3 | 2.78
22 | 0 | 0 | 0 | 15.7 | 3.33
23 | 0 | 0 | 0 | 15.1 | 3.33
24 | 0 | 0 | 0 | 14.6 | 0.56
25 | 0 | 0 | 0 | 14.1 | 1.94
26 | 0 | 0 | 0 | 14.2 | 1.67
27 | 0 | 0 | 0 | 14.2 | 2.22
28 | 0 | 0 | 0 | 14.1 | 2.22
29 | 0 | 0 | 0 | 13.9 | 2.22
30 | 13.9 | 8.3 | 10.5 | 14.2 | 2.22
31 | 175 | 72.2 | 401.4 | 15 | 2.78
32 | 377.8 | 200 | 387.4 | 18.8 | 3.33
33 | 588.9 | 238.9 | 560.3 | 21.1 | 2.78
34 | 683.3 | 352.8 | 445.6 | 22.5 | 6.11
35 | 727.8 | 325 | 502 | 22.3 | 5
36 | 847.2 | 352.8 | 616.2 | 24.5 | 5.56
37 | 777.8 | 291.7 | 655.3 | 23.9 | 5.56
38 | 580.6 | 244.4 | 538.1 | 23.7 | 5.56
39 | 341.7 | 158.3 | 399.5 | 23.8 | 5.56
40 | 136.1 | 72.2 | 249.5 | 22.5 | 4.44
41 | 11.1 | 5.6 | 10.5 | 21.1 | 4.44
42 | 0 | 0 | 0 | 20.2 | 3.33
43 | 0 | 0 | 0 | 18.1 | 3.89
44 | 0 | 0 | 0 | 17.4 | 2.78
45 | 0 | 0 | 0 | 16.5 | 2.78
46 | 0 | 0 | 0 | 16.3 | 2.22
47 | 0 | 0 | 0 | 15.4 | 2.78
48 | 0 | 0 | 0 | 15.5 | 0.83
49 | 0 | 0 | 0 | 15.2 | 3.33
50 | 0 | 0 | 0 | 14.8 | 2.22
51 | 0 | 0 | 0 | 14.5 | 2.22
52 | 0 | 0 | 0 | 14.3 | 2.78
53 | 0 | 0 | 0 | 13.9 | 3.33
54 | 19.4 | 11.1 | 11.1 | 14 | 2.78
55 | 188.9 | 97.2 | 357.3 | 14.5 | 1.67
56 | 313.9 | 222.2 | 199.4 | 16.8 | 2.22
57 | 375 | 272.2 | 164.3 | 19.6 | 4.44
58 | 725 | 425 | 404 | 22.4 | 5
59 | 952.8 | 405.6 | 681.2 | 22.2 | 6.11
60 | 926.7 | 170.1 | 906.8 | 24 | 5.56
61 | 831.1 | 163 | 865 | 24.4 | 5
62 | 716.7 | 119.4 | 955 | 24.9 | 5.56
63 | 547.2 | 88.9 | 884.4 | 24.7 | 3.89
64 | 291.7 | 72.2 | 693.8 | 23.4 | 4.44
65 | 38.9 | 22.2 | 11.1 | 21.6 | 4.44
66 | 0 | 0 | 0 | 20.3 | 2.5
67 | 0 | 0 | 0 | 20.2 | 2.22
68 | 0 | 0 | 0 | 17.7 | 2.22
69 | 0 | 0 | 0 | 18.7 | 2.22
70 | 0 | 0 | 0 | 18.2 | 1.67
71 | 0 | 0 | 0 | 18 | 1.67
72 | 0 | 0 | 0 | 17.4 | 1.11
73 | 0 | 0 | 0 | 16.2 | 1.67
74 | 0 | 0 | 0 | 15.3 | 1.94
75 | 0 | 0 | 0 | 15 | 1.67
76 | 0 | 0 | 0 | 15.2 | 2.78
77 | 0 | 0 | 0 | 15.3 | 2.78
78 | 5.6 | 10.8 | 27.3 | 15.2 | 2.78
79 | 127.8 | 76.3 | 425.3 | 15.9 | 2.78
80 | 477.8 | 133.3 | 748.2 | 18.6 | 2.22
81 | 641.7 | 252.8 | 621 | 20.9 | 2.22
82 | 769.4 | 275 | 665 | 22 | 2.78
83 | 786.1 | 266.7 | 645.9 | 23.5 | 1.67
84 | 926.7 | 170.1 | 906.8 | 25 | 2.78
85 | 863.9 | 136.1 | 978.8 | 25.6 | 2.22
86 | 713.9 | 116.7 | 953.7 | 26.3 | 2.22
87 | 472.2 | 105.6 | 796.5 | 26.3 | 2.78
88 | 258.3 | 72.2 | 694.7 | 25.9 | 2.22
89 | 27.8 | 11.1 | 11.9 | 24.3 | 2.22
90 | 0 | 0 | 0 | 21.5 | 1.67
91 | 0 | 0 | 0 | 20.1 | 1.39
92 | 0 | 0 | 0 | 19.3 | 1.67
93 | 0 | 0 | 0 | 18.5 | 1.39
94 | 0 | 0 | 0 | 17.5 | 1.67
95 | 0 | 0 | 0 | 17 | 1.67
96 | 0 | 0 | 0 | 16.8 | 1.39
97 | 0 | 0 | 0 | 16.5 | 2.22
98 | 0 | 0 | 0 | 16.4 | 2.22
99 | 0 | 0 | 0 | 16 | 3.33
100 | 0 | 0 | 0 | 16.1 | 2.22
101 | 0 | 0 | 0 | 16.1 | 2.78
102 | 8.3 | 2.8 | 12.7 | 16.1 | 2.78
103 | 169.4 | 100 | 269.4 | 16.5 | 1.67
104 | 327.8 | 219.4 | 234.9 | 18.1 | 2.22
105 | 536.1 | 325 | 336.6 | 19.3 | 2.78
106 | 813.9 | 322.2 | 660.4 | 20.9 | 2.78
107 | 566.7 | 363.9 | 251.8 | 22.8 | 2.78
108 | 780.6 | 291.7 | 607.1 | 23.4 | 2.22
109 | 666.7 | 316.7 | 470.1 | 24.1 | 1.67
110 | 558.3 | 194.4 | 580.3 | 24.8 | 2.22
111 | 513.9 | 97.2 | 885.3 | 24.7 | 1.67
112 | 250 | 72.2 | 689.7 | 24.5 | 1.39
113 | 38.9 | 11.1 | 12.7 | 23.3 | 1.67
114 | 0 | 0 | 0 | 21 | 1.67
115 | 0 | 0 | 0 | 19.5 | 1.67
116 | 0 | 0 | 0 | 18.6 | 1.67
117 | 0 | 0 | 0 | 17.8 | 2.78
118 | 0 | 0 | 0 | 17.1 | 2.22
119 | 0 | 0 | 0 | 16.3 | 2.22
120 | 0 | 0 | 0 | 16 | 1.67
121 | 0 | 0 | 0 | 15.8 | 2.22
122 | 0 | 0 | 0 | 15.9 | 2.22
123 | 0 | 0 | 0 | 15.9 | 2.78
124 | 0 | 0 | 0 | 15.9 | 1.67
125 | 0 | 0 | 0 | 15.8 | 1.67
126 | 13.9 | 8.3 | 13.6 | 15.7 | 2.78
127 | 83.3 | 72.2 | 43 | 15.8 | 2.78
128 | 147.2 | 133.3 | 30.1 | 16.7 | 2.22
129 | 272.2 | 252.8 | 31 | 18.4 | 2.78
130 | 511.1 | 380.6 | 175.1 | 21 | 2.22
131 | 875 | 333.3 | 671.7 | 22 | 2.78
132 | 827.8 | 322.2 | 627 | 23 | 2.22
133 | 775 | 233.3 | 726.5 | 25 | 3.33
134 | 655.6 | 205.6 | 716.5 | 24.3 | 2.22
135 | 430.6 | 180.6 | 541.2 | 24.3 | 3.33
136 | 255.6 | 83.3 | 666.4 | 23.9 | 2.22
137 | 38.9 | 13.9 | 13.6 | 22.4 | 2.22
138 | 0 | 0 | 0 | 20.3 | 1.67
139 | 0 | 0 | 0 | 18.9 | 1.67
140 | 0 | 0 | 0 | 17.8 | 1.67
141 | 0 | 0 | 0 | 17.2 | 2.22
142 | 0 | 0 | 0 | 17 | 2.22
143 | 0 | 0 | 0 | 16 | 1.67
144 | 0 | 0 | 0 | 15.5 | 1.94
145 | 0 | 0 | 0 | 15 | 1.94
146 | 0 | 0 | 0 | 14.5 | 2.22
147 | 0 | 0 | 0 | 14.7 | 1.94
148 | 0 | 0 | 0 | 15 | 1.67
149 | 0 | 0 | 0 | 15 | 2.22
150 | 11.1 | 2.8 | 14.7 | 15 | 2.22
151 | 127.8 | 75 | 203.7 | 15.8 | 2.22
152 | 491.7 | 141.7 | 756.3 | 18.5 | 1.67
153 | 538.9 | 227.8 | 494.5 | 21 | 2.22
154 | 747.2 | 255.6 | 658.5 | 23.3 | 3.89
155 | 936.1 | 155.6 | 966.6 | 23.8 | 3.33
156 | 925 | 138.9 | 973.5 | 24.8 | 2.22
157 | 841.7 | 136.1 | 944.9 | 25.6 | 3.89
158 | 691.7 | 152.8 | 856.6 | 25.9 | 3.89
159 | 519.4 | 161.1 | 774.3 | 25.8 | 3.89
160 | 166.7 | 80.6 | 332.3 | 24.5 | 3.89
161 | 19.4 | 11.1 | 14.7 | 22.5 | 2.78
162 | 0 | 0 | 0 | 20.3 | 2.78
163 | 0 | 0 | 0 | 19.2 | 2.78
164 | 0 | 0 | 0 | 18.6 | 2.22
165 | 0 | 0 | 0 | 18.2 | 2.22
166 | 0 | 0 | 0 | 17.9 | 2.78
167 | 0 | 0 | 0 | 17.2 | 3.33
168 | 0 | 0 | 0 | 16.4 | 2.22
169 | 0 | 0 | 0 | 16.4 | 1.39
170 | 0 | 0 | 0 | 16.2 | 3.89
171 | 0 | 0 | 0 | 16.3 | 4.44
172 | 0 | 0 | 0 | 16.2 | 2.78
173 | 0 | 0 | 0 | 15.8 | 2.22
174 | 11.1 | 2.8 | 15.8 | 15.2 | 1.67
175 | 108.3 | 86.1 | 85.5 | 15.6 | 1.94
176 | 447.2 | 188.9 | 557.1 | 19.1 | 3.33
177 | 630.6 | 197.2 | 687.7 | 21.4 | 2.78
178 | 852.8 | 183.3 | 895.2 | 21.9 | 2.22
179 | 908.3 | 163.9 | 920.5 | 24.1 | 1.67
180 | 930.6 | 130.6 | 989.2 | 25.2 | 3.33
181 | 863.9 | 113.9 | 995.5 | 26.2 | 2.22
182 | 722.2 | 102.8 | 961 | 27 | 2.22
183 | 513.9 | 80.6 | 886.8 | 26.5 | 3.89
184 | 258.3 | 55.6 | 698.7 | 25.8 | 3.33
185 | 38.9 | 8.3 | 15.8 | 23.4 | 2.22
186 | 0 | 0 | 0 | 20.5 | 3.89
187 | 0 | 0 | 0 | 18.9 | 2.78
188 | 0 | 0 | 0 | 17.8 | 2.78
189 | 0 | 0 | 0 | 17 | 2.78
190 | 0 | 0 | 0 | 16.4 | 2.78
191 | 0 | 0 | 0 | 16.5 | 2.78
192 | 0 | 0 | 0 | 16 | 2.5
193 | 0 | 0 | 0 | 15.7 | 2.78
194 | 0 | 0 | 0 | 16 | 2.22
195 | 0 | 0 | 0 | 15.8 | 2.22
196 | 0 | 0 | 0 | 16 | 3.89
197 | 0 | 0 | 0 | 16.1 | 3.89
198 | 16.7 | 8.3 | 17 | 15.9 | 2.78
199 | 213.9 | 69.4 | 554.1 | 15.8 | 2.22
200 | 305.6 | 183.3 | 263 | 17.6 | 2.78
201 | 575 | 250 | 514.8 | 20.9 | 2.78
202 | 661.1 | 319.4 | 456.1 | 21.6 | 2.78
203 | 913.8 | 136.1 | 870.7 | 23.1 | 5
204 | 941.7 | 86.1 | 1010 | 23.9 | 4.44
205 | 866.7 | 91.7 | 995.8 | 24.4 | 5.56
206 | 719.4 | 86.1 | 961.4 | 24.8 | 1.67
207 | 522.2 | 77.8 | 887.4 | 24.4 | 4.44
208 | 269.4 | 47.2 | 699.8 | 23.8 | 5
209 | 30.6 | 8.3 | 17 | 22.1 | 3.89
210 | 0 | 0 | 0 | 19.8 | 3.33
211 | 0 | 0 | 0 | 18.7 | 2.78
212 | 0 | 0 | 0 | 17.7 | 2.78
213 | 0 | 0 | 0 | 17.1 | 2.22
214 | 0 | 0 | 0 | 16.4 | 2.22
215 | 0 | 0 | 0 | 15.9 | 2.78
216 | 0 | 0 | 0 | 15.5 | 2.78
217 | 0 | 0 | 0 | 15.1 | 2.78
218 | 0 | 0 | 0 | 15 | 1.94
219 | 0 | 0 | 0 | 14.7 | 1.94
220 | 0 | 0 | 0 | 14 | 2.78
221 | 0 | 0 | 0 | 13.5 | 2.78
222 | 22.2 | 8.3 | 18.3 | 13.4 | 2.22
223 | 191.7 | 91.7 | 382.4 | 13.5 | 1.94
224 | 452.8 | 155.6 | 638.2 | 16.8 | 2.22
225 | 680.6 | 169.4 | 808.2 | 20.2 | 4.44
226 | 827.8 | 188.9 | 851.5 | 22.2 | 3.33
227 | 952.8 | 127.8 | 1010.3 | 23.6 | 4.44
228 | 950 | 105.6 | 1010.3 | 24.3 | 3.33
229 | 883.3 | 94.4 | 996.1 | 25.2 | 4.44
230 | 741.7 | 83.3 | 961.8 | 25.4 | 5
231 | 519.4 | 86.1 | 888 | 25.4 | 4.44
232 | 291.7 | 63.9 | 701 | 24.3 | 4.44
233 | 47.2 | 5.6 | 18.3 | 22.2 | 4.44
234 | 0 | 0 | 0 | 19.8 | 2.78
235 | 0 | 0 | 0 | 18.4 | 2.78
236 | 0 | 0 | 0 | 17.7 | 2.78
237 | 0 | 0 | 0 | 17.2 | 2.78
238 | 0 | 0 | 0 | 16.8 | 2.78
239 | 0 | 0 | 0 | 16.8 | 2.78
240 | 0 | 0 | 0 | 16.7 | 3.06
241 | 0 | 0 | 0 | 16.5 | 2.5
242 | 0 | 0 | 0 | 15.8 | 2.78
243 | 0 | 0 | 0 | 15.3 | 2.22
244 | 0 | 0 | 0 | 15.8 | 2.22
245 | 0 | 0 | 0 | 15 | 2.22
246 | 27.8 | 8.3 | 19.8 | 14.7 | 2.22
247 | 236.1 | 63.9 | 656.5 | 15 | 1.67
248 | 519.4 | 88.9 | 888.6 | 17.8 | 2.22
249 | 727.8 | 91.7 | 962.2 | 20.7 | 2.78
250 | 880.6 | 108.3 | 996.4 | 22.5 | 1.67
251 | 958.3 | 108.3 | 1010.6 | 24.5 | 1.67
252 | 944.4 | 102.8 | 1010.6 | 25.1 | 2.22
253 | 863.9 | 105.6 | 996.4 | 26.1 | 3.33
254 | 713.9 | 97.2 | 962.2 | 26.1 | 2.78
255 | 502.8 | 91.7 | 880.8 | 26 | 1.67
256 | 258.3 | 61.1 | 702.2 | 25.8 | 2.22
257 | 36.1 | 11.1 | 19.8 | 24 | 2.78
258 | 0 | 0 | 0 | 21.5 | 2.78
259 | 0 | 0 | 0 | 20.1 | 2.78
260 | 0 | 0 | 0 | 19 | 2.78
261 | 0 | 0 | 0 | 18.5 | 2.78
262 | 0 | 0 | 0 | 17.6 | 2.22
263 | 0 | 0 | 0 | 17.2 | 2.78
264 | 0 | 0 | 0 | 17 | 3.33
265 | 0 | 0 | 0 | 17.2 | 1.67
266 | 0 | 0 | 0 | 16.9 | 1.67
267 | 0 | 0 | 0 | 16.5 | 1.67
268 | 0 | 0 | 0 | 16.3 | 3.89
269 | 0 | 0 | 0 | 16.2 | 3.89
270 | 2.8 | 0 | 21.4 | 16.1 | 2.78
271 | 166.7 | 61.1 | 401 | 16.3 | 2.78
272 | 508.3 | 94.4 | 884.6 | 19.4 | 2.78
273 | 716.7 | 116.7 | 945 | 22 | 3.89
274 | 858.3 | 125 | 973.8 | 24 | 3.33
275 | 933.3 | 122.2 | 996.2 | 25.5 | 3.89
276 | 930.6 | 144.4 | 965.5 | 26.6 | 3.33
277 | 891.7 | 194.4 | 925.8 | 27 | 3.33
278 | 586.1 | 208.3 | 595 | 27.5 | 2.78
279 | 275 | 141.7 | 285 | 27.7 | 1.94
280 | 136.1 | 83.3 | 200.5 | 27 | 2.78
281 | 19.4 | 16.7 | 21.4 | 25 | 1.67
282 | 0 | 0 | 0 | 22.2 | 2.78
283 | 0 | 0 | 0 | 21 | 2.78
284 | 0 | 0 | 0 | 20 | 2.22
285 | 0 | 0 | 0 | 19.2 | 2.78
286 | 0 | 0 | 0 | 18.2 | 2.78
287 | 0 | 0 | 0 | 17.5 | 2.22
288 | 0 | 0 | 0 | 17.6 | 3.61
289 | 0 | 0 | 0 | 17.7 | 4.44
290 | 0 | 0 | 0 | 17.7 | 4.44
291 | 0 | 0 | 0 | 17.7 | 2.78
292 | 0 | 0 | 0 | 17.7 | 2.78
293 | 0 | 0 | 0 | 17.5 | 2.78
294 | 5.6 | 8.3 | 0 | 17.7 | 2.22
295 | 94.4 | 88.9 | 21 | 17.9 | 1.67
296 | 366.7 | 219.4 | 313.9 | 19 | 1.67
297 | 613.9 | 291.7 | 506.4 | 21.6 | 2.22
298 | 719.4 | 327.8 | 519.1 | 23.1 | 2.22
299 | 691.7 | 341.7 | 429.1 | 24.1 | 2.22
300 | 822.2 | 380.6 | 541.4 | 24.7 | 1.67
301 | 558.3 | 338.9 | 290.8 | 25.7 | 1.39
302 | 611.1 | 313.9 | 467.1 | 26.1 | 2.22
303 | 294.4 | 163.9 | 278.4 | 26.3 | 2.78
304 | 161.1 | 91.7 | 262.9 | 25.6 | 2.78
305 | 19.4 | 16.7 | 23.1 | 24.1 | 2.78
306 | 0 | 0 | 0 | 22.7 | 2.22
307 | 0 | 0 | 0 | 21.8 | 2.22
308 | 0 | 0 | 0 | 20.3 | 2.78
309 | 0 | 0 | 0 | 19.6 | 2.78
310 | 0 | 0 | 0 | 18.6 | 2.78
311 | 0 | 0 | 0 | 17.8 | 3.33
312 | 0 | 0 | 0 | 17.7 | 3.89
313 | 0 | 0 | 0 | 17.6 | 2.5
314 | 0 | 0 | 0 | 17.1 | 2.5
315 | 0 | 0 | 0 | 16.5 | 1.67
316 | 0 | 0 | 0 | 15.7 | 2.22
317 | 0 | 0 | 0 | 15.3 | 1.11
318 | 11.1 | 5.6 | 25 | 15.3 | 1.67
319 | 113.9 | 83.3 | 115.2 | 15.6 | 1.39
320 | 266.7 | 194.4 | 153.6 | 17.5 | 2.78
321 | 666.7 | 180.6 | 762.4 | 21.6 | 1.67
322 | 827.8 | 188.9 | 845 | 24.7 | 2.78
323 | 916.7 | 247.2 | 819.1 | 26.1 | 2.22
324 | 736.1 | 233.3 | 615.1 | 26.9 | 2.22
325 | 636.1 | 216.7 | 554.8 | 27.2 | 3.89
326 | 713.9 | 163.9 | 862.6 | 27.7 | 2.78
327 | 394.4 | 136.1 | 549.4 | 27.7 | 1.67
328 | 275 | 105.6 | 639.1 | 26.6 | 2.22
329 | 33.3 | 13.9 | 25 | 25 | 1.39
330 | 0 | 0 | 0 | 22.8 | 2.22
331 | 0 | 0 | 0 | 21.2 | 1.39
332 | 0 | 0 | 0 | 20.2 | 3.89
333 | 0 | 0 | 0 | 19.5 | 2.22
334 | 0 | 0 | 0 | 18.6 | 2.22
335 | 0 | 0 | 0 | 18 | 2.22
336 | 0 | 0 | 0 | 18 | 4.17
337 | 0 | 0 | 0 | 18 | 2.78
338 | 0 | 0 | 0 | 17.8 | 2.78
339 | 0 | 0 | 0 | 17.5 | 2.22
340 | 0 | 0 | 0 | 17.3 | 1.67
341 | 0 | 0 | 0 | 17.2 | 2.22
342 | 5.6 | 0 | 27 | 16.5 | 2.78
343 | 161.1 | 69.4 | 344.4 | 16.8 | 1.39
344 | 469.4 | 108.3 | 766 | 19.3 | 1.67
345 | 700 | 119.4 | 908.4 | 23.3 | 1.39
346 | 847.2 | 141.7 | 931.3 | 25.3 | 2.78
347 | 936.1 | 136.1 | 976.8 | 26.3 | 2.22
348 | 947.2 | 127.8 | 1000.6 | 26.6 | 2.78
349 | 875 | 125 | 990 | 27 | 2.78
350 | 741.7 | 111.1 | 964 | 27.3 | 1.67
351 | 541.7 | 91.7 | 891.3 | 27.3 | 2.22
352 | 288.9 | 69.4 | 707.6 | 26.8 | 1.67
353 | 50 | 19.4 | 27 | 25 | 1.67
354 | 0 | 0 | 0 | 22.6 | 1.67
355 | 0 | 0 | 0 | 21.8 | 1.67
356 | 0 | 0 | 0 | 19.7 | 2.22
357 | 0 | 0 | 0 | 19.3 | 3.33
358 | 0 | 0 | 0 | 18 | 3.33
359 | 0 | 0 | 0 | 17.3 | 2.78
360 | 0 | 0 | 0 | 17.3 | 4.44
361 | 0 | 0 | 0 | 17 | 3.33
362 | 0 | 0 | 0 | 17 | 2.78
363 | 0 | 0 | 0 | 16.9 | 1.67
364 | 0 | 0 | 0 | 17.1 | 2.22
365 | 0 | 0 | 0 | 17.2 | 3.33
366 | 27.8 | 11.1 | 29.2 | 17.2 | 1.67
367 | 169.4 | 94.4 | 280.7 | 17.7 | 2.22
368 | 383.3 | 219.4 | 346.7 | 20 | 2.78
369 | 602.8 | 180.6 | 659.2 | 21.6 | 4.44
370 | 805.6 | 163.9 | 845.2 | 24.4 | 3.33
371 | 961.1 | 213.9 | 910.5 | 25 | 2.78
372 | 919.4 | 222.2 | 849.6 | 26 | 2.78
373 | 555.6 | 238.9 | 417.1 | 27.4 | 1.67
374 | 663.9 | 127.8 | 837 | 27.1 | 3.33
375 | 547.2 | 136.1 | 869.7 | 27.6 | 3.33
376 | 180.6 | 77.8 | 384.7 | 26.7 | 3.89
377 | 16.7 | 11.1 | 29.2 | 24.8 | 3.89
378 | 0 | 0 | 0 | 22.3 | 2.78
379 | 0 | 0 | 0 | 21.7 | 1.67
380 | 0 | 0 | 0 | 20.4 | 5
381 | 0 | 0 | 0 | 20 | 4.44
382 | 0 | 0 | 0 | 18.9 | 3.33
383 | 0 | 0 | 0 | 17.9 | 2.22
384 | 0 | 0 | 0 | 17.9 | 4.72
385 | 0 | 0 | 0 | 16.7 | 2.78
386 | 0 | 0 | 0 | 16.4 | 2.78
387 | 0 | 0 | 0 | 16.4 | 2.78
388 | 0 | 0 | 0 | 15.8 | 2.78
389 | 0 | 0 | 0 | 15.4 | 3.33
390 | 22.2 | 8.3 | 31.5 | 15.2 | 2.78
391 | 244.4 | 63.9 | 673.1 | 15.9 | 2.22
392 | 527.8 | 77.8 | 892.7 | 19 | 2.78
393 | 750 | 80.6 | 965 | 22.3 | 3.89
394 | 894.4 | 80.6 | 998.7 | 24.1 | 4.44
395 | 972.2 | 83.3 | 1012.6 | 25.6 | 5.56
396 | 969.4 | 88.9 | 1012.6 | 25.9 | 4.44
397 | 875 | 88.9 | 998.7 | 26.7 | 2.78
398 | 741.7 | 91.7 | 965 | 26.8 | 4.44
399 | 538.9 | 75 | 892.7 | 26.7 | 3.89
400 | 283.3 | 52.8 | 710.6 | 25.8 | 2.78
401 | 44.4 | 13.9 | 31.5 | 24.1 | 5
402 | 0 | 0 | 0 | 21 | 3.33
403 | 0 | 0 | 0 | 19.3 | 3.33
404 | 0 | 0 | 0 | 18.4 | 3.33
405 | 0 | 0 | 0 | 17.8 | 3.33
406 | 0 | 0 | 0 | 16.8 | 3.89
407 | 0 | 0 | 0 | 16.2 | 2.78
408 | 0 | 0 | 0 | 16.1 | 5
409 | 0 | 0 | 0 | 15.4 | 2.22
410 | 0 | 0 | 0 | 14.6 | 2.22
411 | 0 | 0 | 0 | 14.1 | 2.78
412 | 0 | 0 | 0 | 13.9 | 2.22
413 | 0 | 0 | 0 | 13.4 | 1.67
414 | 30.6 | 13.9 | 34 | 13.4 | 2.22
415 | 244.4 | 91.7 | 567.2 | 14.4 | 2.22
416 | 480.6 | 150 | 695.3 | 18.1 | 2.22
417 | 747.2 | 119.4 | 965.5 | 20.8 | 5
418 | 824.6 | 197 | 806.5 | 23 | 5.56
419 | 913.8 | 184 | 870.7 | 24.4 | 5
420 | 926.7 | 170.1 | 906.8 | 25.5 | 4.44
421 | 831.1 | 163 | 865 | 26.2 | 4.44
422 | 695.4 | 149.2 | 834.9 | 26.5 | 3.89
423 | 496.9 | 122.1 | 764 | 26.6 | 3.89
424 | 251.5 | 84.4 | 578.2 | 25.6 | 3.89
425 | 35.2 | 17.1 | 32.8 | 23.5 | 3.89
426 | 0 | 0 | 0 | 20.9 | 3.33
427 | 0 | 0 | 0 | 19.4 | 2.22
428 | 0 | 0 | 0 | 18.1 | 2.22
429 | 0 | 0 | 0 | 17.8 | 2.78
430 | 0 | 0 | 0 | 17.4 | 3.33
431 | 0 | 0 | 0 | 16.6 | 2.22
432 | 0 | 0 | 0 | 15.9 | 5.28
433 | 0 | 0 | 0 | 15.3 | 2.22
434 | 0 | 0 | 0 | 14.9 | 2.78
435 | 0 | 0 | 0 | 14.6 | 2.22
436 | 0 | 0 | 0 | 14.5 | 2.22
437 | 0 | 0 | 0 | 14.2 | 1.94
438 | 19.1 | 10.8 | 27.3 | 14.1 | 2.22
439 | 193.7 | 76.3 | 425.3 | 14.1 | 1.67
440 | 451.4 | 135.7 | 641.5 | 16.3 | 1.67
441 | 665 | 166.9 | 752.8 | 20.7 | 2.22
442 | 824.6 | 197 | 806.5 | 23.1 | 2.22
443 | 983.3 | 130.6 | 1013.4 | 24.5 | 3.33
444 | 963.9 | 155.6 | 978.6 | 25.7 | 2.78
445 | 905.6 | 152.8 | 984.8 | 27 | 2.22
446 | 730.6 | 150 | 899.7 | 26.9 | 2.78
447 | 496.9 | 122.2 | 764 | 27 | 3.89
448 | 225 | 77.8 | 544.3 | 26 | 2.78
449 | 22.2 | 16.7 | 36.6 | 24.2 | 1.67
450 | 0 | 0 | 0 | 21.5 | 2.22
451 | 0 | 0 | 0 | 20.1 | 2.22
452 | 0 | 0 | 0 | 18.9 | 2.22
453 | 0 | 0 | 0 | 18.3 | 2.78
454 | 0 | 0 | 0 | 17 | 1.94
455 | 0 | 0 | 0 | 16.5 | 2.5
456 | 0 | 0 | 0 | 15.9 | 5.56
457 | 0 | 0 | 0 | 15.5 | 3.33
458 | 0 | 0 | 0 | 14.8 | 2.78
459 | 0 | 0 | 0 | 14.8 | 2.22
460 | 0 | 0 | 0 | 14.7 | 2.22
461 | 0 | 0 | 0 | 14 | 2.22
462 | 16.7 | 16.7 | 0 | 14.2 | 1.94
463 | 222.2 | 72.2 | 552.1 | 14.6 | 2.22
464 | 441.7 | 136.1 | 638.9 | 19.6 | 1.39
465 | 769.4 | 161.1 | 940.4 | 22.7 | 2.22
466 | 869.4 | 191.7 | 884.6 | 23.9 | 2.22
467 | 983.3 | 152.8 | 1003.2 | 25.5 | 3.33
468 | 977.8 | 147.2 | 1003.2 | 27 | 2.78
469 | 788.9 | 211.1 | 754.1 | 27.2 | 2.78
470 | 483.3 | 272.2 | 326.3 | 26.9 | 2.22
471 | 483.3 | 183.3 | 627.3 | 27.2 | 2.22
472 | 183.3 | 136.1 | 173.8 | 26.2 | 2.78
473 | 22.2 | 22.2 | 0 | 24 | 3.89
474 | 0 | 0 | 0 | 21.6 | 2.78
475 | 0 | 0 | 0 | 20.2 | 2.78
476 | 0 | 0 | 0 | 19.3 | 2.78
477 | 0 | 0 | 0 | 18.3 | 2.78
478 | 0 | 0 | 0 | 17.4 | 2.22
479 | 0 | 0 | 0 | 16.9 | 1.67
480 | 0 | 0 | 0 | 16.2 | 5.83
481 | 0 | 0 | 0 | 16.2 | 2.78
482 | 0 | 0 | 0 | 15.2 | 2.22
483 | 0 | 0 | 0 | 15.3 | 2.22
484 | 0 | 0 | 0 | 15 | 1.67
485 | 0 | 0 | 0 | 14.2 | 1.67
486 | 25 | 22.2 | 42.5 | 14.3 | 2.22
487 | 247.2 | 69.4 | 651.5 | 15.4 | 2.22
488 | 533.3 | 100 | 895.9 | 19.3 | 1.67
489 | 744.4 | 138.9 | 933.6 | 22.6 | 1.67
490 | 888.9 | 158.3 | 951.2 | 23.9 | 2.22
491 | 963.9 | 163.9 | 964 | 24.7 | 3.33
492 | 950 | 191.7 | 913.8 | 25.6 | 5.56
493 | 886.1 | 172.2 | 929.5 | 26.4 | 3.89
494 | 716.7 | 194.4 | 805.1 | 26.1 | 2.78
495 | 544.4 | 119.4 | 885.9 | 26.4 | 3.33
496 | 272.2 | 108.3 | 600.6 | 25.6 | 2.78
497 | 47.2 | 33.3 | 42.5 | 23.8 | 4.44
498 | 0 | 0 | 0 | 21.1 | 2.78
499 | 0 | 0 | 0 | 19.4 | 2.78
500 | 0 | 0 | 0 | 18.6 | 3.89
501 | 0 | 0 | 0 | 17.6 | 2.78
502 | 0 | 0 | 0 | 16.9 | 2.78
503 | 0 | 0 | 0 | 16.3 | 2.78
504 | 0 | 0 | 0 | 15.6 | 6.11
505 | 0 | 0 | 0 | 15.4 | 3.89
506 | 0 | 0 | 0 | 15.1 | 3.33
507 | 0 | 0 | 0 | 14.8 | 2.22
508 | 0 | 0 | 0 | 14.3 | 2.22
509 | 0 | 0 | 0 | 13.9 | 3.33
510 | 13.9 | 16.7 | 0 | 14 | 2.22
511 | 111.1 | 88.9 | 81.1 | 14.1 | 2.22
512 | 513.9 | 138.9 | 779.2 | 16.7 | 2.78
513 | 716.7 | 125 | 909.8 | 21.5 | 3.89
514 | 930.6 | 108.3 | 1000.9 | 23.6 | 5
515 | 1000 | 122.2 | 1014.6 | 24.3 | 5
516 | 986.1 | 158.3 | 995.1 | 25.1 | 6.11
517 | 863.9 | 175 | 894.7 | 25.3 | 5.56
518 | 738.9 | 161.1 | 888.4 | 26 | 5
519 | 519.4 | 141.7 | 785 | 15.5 | 4.44
520 | 255.6 | 86.1 | 618.1 | 24.5 | 4.44
521 | 27.8 | 22.2 | 45.6 | 22.5 | 5
522 | 0 | 0 | 0 | 20.6 | 4.44
523 | 0 | 0 | 0 | 19 | 3.89
524 | 0 | 0 | 0 | 18.1 | 2.78
525 | 0 | 0 | 0 | 17.6 | 4.44
526 | 0 | 0 | 0 | 16.8 | 3.89
527 | 0 | 0 | 0 | 15.8 | 3.33
528 | 0 | 0 | 0 | 15.3 | 6.39
529 | 0 | 0 | 0 | 14.7 | 1.67
530 | 0 | 0 | 0 | 13.7 | 1.39
531 | 0 | 0 | 0 | 13.1 | 2.22
532 | 0 | 0 | 0 | 12.9 | 1.39
533 | 0 | 0 | 0 | 12.3 | 1.39
534 | 38.9 | 16.7 | 49 | 12.1 | 1.67
535 | 291.7 | 55.6 | 720.4 | 13.8 | 1.39
536 | 577.8 | 75 | 897.6 | 17.4 | 2.78
537 | 797.2 | 80.6 | 968.3 | 19.4 | 3.33
538 | 933.3 | 86.1 | 1001.3 | 21.7 | 5
539 | 1000 | 88.9 | 1015 | 23.8 | 3.33
540 | 991.7 | 86.1 | 1015 | 25.1 | 4.44
541 | 902.8 | 88.9 | 1001.3 | 26.7 | 5
542 | 755.6 | 86.1 | 968.3 | 26.6 | 3.89
543 | 547.2 | 86.1 | 897.6 | 26.7 | 3.89
544 | 280.6 | 63.9 | 720.4 | 26.1 | 3.89
545 | 36.1 | 19.4 | 49 | 24.4 | 3.89
546 | 0 | 0 | 0 | 21.2 | 3.89
547 | 0 | 0 | 0 | 17.6 | 2.78
548 | 0 | 0 | 0 | 18.3 | 2.78
549 | 0 | 0 | 0 | 17.3 | 2.78
550 | 0 | 0 | 0 | 16.5 | 1.67
551 | 0 | 0 | 0 | 16 | 2.22
552 | 0 | 0 | 0 | 15.3 | 6.67
553 | 0 | 0 | 0 | 15.2 | 2.22
554 | 0 | 0 | 0 | 14.3 | 2.5
555 | 0 | 0 | 0 | 13.8 | 1.94
556 | 0 | 0 | 0 | 13.4 | 1.94
557 | 0 | 0 | 0 | 13.2 | 1.94
558 | 19.1 | 10.8 | 27.3 | 13 | 1.67
559 | 193.7 | 76.3 | 425.3 | 13 | 2.22
560 | 451.4 | 135.7 | 641.5 | 17.1 | 2.22
561 | 665 | 166.9 | 752.8 | 19 | 2.78
562 | 824.6 | 197 | 806.5 | 21.7 | 2.78
563 | 913.8 | 184 | 870.7 | 23.9 | 3.33
564 | 926.7 | 170.1 | 906.8 | 25.2 | 3.89
565 | 886.1 | 83.3 | 1001.8 | 26.4 | 4.44
566 | 738.9 | 80.6 | 968.9 | 26.7 | 3.89
567 | 455.6 | 150 | 630.8 | 27.3 | 3.33
568 | 202.8 | 163.9 | 140.5 | 26.9 | 4.44
569 | 38.9 | 19.4 | 52.5 | 24.7 | 4.44
570 | 0 | 0 | 0 | 21.4 | 3.89
571 | 0 | 0 | 0 | 20.1 | 2.78
572 | 0 | 0 | 0 | 18.9 | 2.78
573 | 0 | 0 | 0 | 18.5 | 3.33
574 | 0 | 0 | 0 | 17.6 | 2.78
575 | 0 | 0 | 0 | 16.7 | 2.78
576 | 0 | 0 | 0 | 16.4 | 6.94
577 | 0 | 0 | 0 | 16.6 | 1.67
578 | 0 | 0 | 0 | 16.3 | 1.39
579 | 0 | 0 | 0 | 15 | 1.67
580 | 0 | 0 | 0 | 15 | 1.67
581 | 0 | 0 | 0 | 15 | 1.67
582 | 41.7 | 16.7 | 56.3 | 14.3 | 2.22
583 | 288.9 | 41.7 | 723.9 | 15.5 | 1.67
584 | 566.7 | 58.3 | 899.3 | 19.2 | 1.67
585 | 772.2 | 72.2 | 969.5 | 23.2 | 3.33
586 | 916.7 | 80.6 | 1002.3 | 25.8 | 3.33
587 | 991.7 | 80.6 | 1015.9 | 27.5 | 3.33
588 | 983.3 | 94.4 | 1015.9 | 28.2 | 4.44
589 | 905.6 | 111.1 | 1002.3 | 28.4 | 5
590 | 761.1 | 88.9 | 969.5 | 28.5 | 3.33
591 | 561.1 | 80.6 | 899.3 | 28.5 | 2.78
592 | 308.3 | 66.7 | 723.9 | 27.8 | 2.22
593 | 52.8 | 22.2 | 56.3 | 26 | 4.44
594 | 0 | 0 | 0 | 23 | 3.33
595 | 0 | 0 | 0 | 21.5 | 2.78
596 | 0 | 0 | 0 | 20.5 | 2.78
597 | 0 | 0 | 0 | 19.8 | 2.78
598 | 0 | 0 | 0 | 18.7 | 3.33
599 | 0 | 0 | 0 | 17.9 | 3.33
600 | 0 | 0 | 0 | 17.2 | 7.22
601 | 0 | 0 | 0 | 16.7 | 2.22
602 | 0 | 0 | 0 | 16.2 | 2.78
603 | 0 | 0 | 0 | 16 | 2.78
604 | 0 | 0 | 0 | 16.4 | 2.22
605 | 0 | 0 | 0 | 16.2 | 3.89
606 | 30.6 | 30.6 | 0 | 16.2 | 2.78
607 | 263.9 | 75 | 676.1 | 17.2 | 2.22
608 | 527.8 | 111.1 | 854.4 | 19.3 | 2.78
609 | 750 | 100 | 970.1 | 23.1 | 2.22
610 | 888.9 | 111.1 | 999.8 | 24.9 | 3.89
611 | 969.4 | 108.3 | 1016.3 | 27.1 | 4.44
612 | 972.2 | 108.3 | 1016.3 | 27.8 | 3.89
613 | 908.3 | 88.9 | 1002.7 | 28.5 | 4.44
614 | 761.1 | 83.3 | 970.1 | 28.6 | 4.44
615 | 558.3 | 80.6 | 900.2 | 28.6 | 4.44
616 | 297.2 | 69.4 | 725.6 | 27.7 | 4.44
617 | 50 | 22.2 | 60.2 | 25.9 | 3.89
618 | 0 | 0 | 0 | 23.5 | 3.89
619 | 0 | 0 | 0 | 21.5 | 3.33
620 | 0 | 0 | 0 | 20.5 | 3.33
621 | 0 | 0 | 0 | 19.7 | 3.33
622 | 0 | 0 | 0 | 18.7 | 3.89
623 | 0 | 0 | 0 | 17.8 | 3.33
624 | 0 | 0 | 0 | 17.5 | 7.5
625 | 0 | 0 | 0 | 17 | 2.78
626 | 0 | 0 | 0 | 16.2 | 2.22
627 | 0 | 0 | 0 | 15.8 | 2.22
628 | 0 | 0 | 0 | 15.7 | 2.22
629 | 0 | 0 | 0 | 15.3 | 2.22
630 | 25 | 11.1 | 64.3 | 14.6 | 1.67
631 | 258.3 | 61.1 | 702.4 | 15.5 | 2.22
632 | 522.2 | 75 | 901.1 | 20 | 2.22
633 | 747.2 | 80.6 | 970.7 | 23.8 | 3.89
634 | 894.4 | 83.3 | 1003.2 | 25.8 | 3.33
635 | 966.7 | 91.7 | 1016.7 | 26.8 | 5
636 | 966.7 | 105.6 | 1016.7 | 27.9 | 5
637 | 894.4 | 108.3 | 1003.2 | 28.3 | 5
638 | 755.6 | 111.1 | 970.7 | 28.7 | 4.44
639 | 552.8 | 91.7 | 901.1 | 28.3 | 5
640 | 297.2 | 80.6 | 727.5 | 27.5 | 3.89
641 | 58.3 | 30.6 | 64.3 | 25.1 | 6.11
642 | 0 | 0 | 0 | 22.8 | 5
643 | 0 | 0 | 0 | 21.3 | 4.44
644 | 0 | 0 | 0 | 20.5 | 3.89
645 | 0 | 0 | 0 | 20.1 | 4.44
646 | 0 | 0 | 0 | 19.3 | 3.33
647 | 0 | 0 | 0 | 18.4 | 4.44
648 | 0 | 0 | 0 | 17.9 | 7.78
649 | 0 | 0 | 0 | 17.1 | 3.33
650 | 0 | 0 | 0 | 17.1 | 2.22
651 | 0 | 0 | 0 | 17 | 2.22
652 | 0 | 0 | 0 | 16.8 | 1.94
653 | 0 | 0 | 0 | 16.1 | 1.94
654 | 5.6 | 8.3 | 0 | 16.1 | 2.78
655 | 236.1 | 77.8 | 561.1 | 16.4 | 2.78
656 | 419.4 | 111.1 | 627.9 | 19.4 | 2.78
657 | 630.6 | 230.6 | 604.6 | 22 | 3.33
658 | 777.8 | 302.8 | 607.3 | 25 | 3.89
659 | 780.6 | 330.6 | 532.8 | 26.1 | 5
660 | 908.3 | 294.4 | 726.8 | 27.4 | 5.56
661 | 836.1 | 294.4 | 692.5 | 27.9 | 5.56
662 | 611.1 | 319.4 | 440.9 | 27.4 | 5
663 | 641.7 | 286.1 | 724.1 | 27.7 | 3.33
664 | 341.7 | 183.3 | 561.1 | 26.4 | 5.56
665 | 27.8 | 30.6 | 0 | 24.3 | 5.56
666 | 0 | 0 | 0 | 22.5 | 3.89
667 | 0 | 0 | 0 | 21.5 | 2.78
668 | 0 | 0 | 0 | 20.3 | 2.78
669 | 0 | 0 | 0 | 19.7 | 2.78
670 | 0 | 0 | 0 | 19.3 | 2.78
671 | 0 | 0 | 0 | 18.3 | 2.22
672 | 0 | 0 | 0 | 17.8 | 8.06
673 | 0 | 0 | 0 | 17.6 | 2.78
674 | 0 | 0 | 0 | 17.6 | 2.22
675 | 0 | 0 | 0 | 17.1 | 2.78
676 | 0 | 0 | 0 | 16.5 | 2.22
677 | 0 | 0 | 0 | 16.2 | 2.78
678 | 19.4 | 19.4 | 0 | 15.7 | 2.22
679 | 219.4 | 113.9 | 372.2 | 15.7 | 1.67
680 | 550 | 97.2 | 902.9 | 17.4 | 1.67
681 | 777.8 | 119.4 | 971.9 | 23 | 1.94
682 | 911.1 | 130.6 | 995.2 | 25.7 | 2.78
683 | 980.6 | 141.7 | 990.6 | 27.6 | 5
684 | 975 | 133.3 | 993.9 | 28.3 | 5.56
685 | 891.7 | 125 | 977.4 | 28.9 | 4.44
686 | 736.1 | 116.7 | 933.5 | 29 | 4.44
687 | 519.4 | 102.8 | 845.5 | 28.9 | 4.44
688 | 269.4 | 75 | 685.6 | 28.4 | 3.89
689 | 38.9 | 19.4 | 73 | 26.2 | 4.44
690 | 0 | 0 | 0 | 23.5 | 4.44
691 | 0 | 0 | 0 | 22.1 | 3.89
692 | 0 | 0 | 0 | 21.4 | 3.33
693 | 0 | 0 | 0 | 20.5 | 4.44
694 | 0 | 0 | 0 | 19.9 | 3.33
695 | 0 | 0 | 0 | 18.7 | 2.78
696 | 0 | 0 | 0 | 18.3 | 8.33
697 | 0 | 0 | 0 | 17.2 | 2.78
698 | 0 | 0 | 0 | 16.9 | 2.22
699 | 0 | 0 | 0 | 16.6 | 2.22
700 | 0 | 0 | 0 | 16.7 | 2.5
701 | 0 | 0 | 0 | 16.6 | 2.22
702 | 36.1 | 16.7 | 77.6 | 16.3 | 1.94
703 | 280.6 | 58.3 | 733 | 16.1 | 2.22
704 | 555.6 | 80.6 | 903.8 | 20.3 | 2.22
705 | 772.2 | 91.7 | 972.5 | 24 | 2.78
706 | 908.3 | 108.3 | 1004.7 | 26.1 | 5.56
707 | 977.8 | 119.4 | 1010.8 | 27.6 | 5.56
708 | 972.2 | 122.2 | 1001 | 28.7 | 6.67
709 | 888.9 | 122.2 | 974.7 | 29.2 | 7.22
710 | 741.7 | 122.2 | 930.6 | 29.3 | 5
711 | 516.7 | 116.7 | 808.8 | 28.2 | 5
712 | 269.4 | 80.6 | 662.6 | 27.6 | 3.89
713 | 41.7 | 25 | 77.6 | 25.8 | 2.78
714 | 0 | 0 | 0 | 22.9 | 3.89
715 | 0 | 0 | 0 | 21.2 | 2.78
716 | 0 | 0 | 0 | 19.8 | 2.78
717 | 0 | 0 | 0 | 18.9 | 3.33
718 | 0 | 0 | 0 | 17.9 | 2.78
719 | 0 | 0 | 0 | 17.6 | 2.22
720 | 0 | 0 | 0 | 17.3 | 8.61
721 | 0 | 0 | 0 | 16.7 | 1.67
722 | 0 | 0 | 0 | 15.8 | 2.22
723 | 0 | 0 | 0 | 15.8 | 2.22
724 | 0 | 0 | 0 | 15.7 | 2.22
725 | 0 | 0 | 0 | 15.4 | 2.22
726 | 36.1 | 13.9 | 82.4 | 14.4 | 2.22
727 | 291.7 | 63.9 | 734.9 | 15.4 | 2.22
728 | 566.7 | 86.1 | 904.8 | 20.7 | 2.78
729 | 777.8 | 105.6 | 973.2 | 24 | 4.44
730 | 919.4 | 119.4 | 1005.2 | 25.9 | 5.56
731 | 988.9 | 122.2 | 1017.8 | 27 | 6.11
732 | 983.3 | 122.2 | 1011.3 | 27.8 | 5
733 | 902.8 | 119.4 | 993.1 | 28.5 | 4.44
734 | 750 | 113.9 | 952.7 | 28.6 | 5
735 | 538.9 | 94.4 | 895.4 | 28.4 | 5.56
736 | 297.2 | 72.2 | 734.9 | 27.5 | 5
737 | 50 | 19.4 | 82.4 | 25.5 | 4.44
738 | 0 | 0 | 0 | 22.9 | 3.89
739 | 0 | 0 | 0 | 20.6 | 2.22
740 | 0 | 0 | 0 | 19.4 | 2.78
741 | 0 | 0 | 0 | 17.8 | 2.78
742 | 0 | 0 | 0 | 17.6 | 2.78
743 | 0 | 0 | 0 | 17.4 | 2.78
744 | 0 | 0 | 0 | 17.3 | 0.28
745 | 0 | 0 | 0 | 17 | 2.22
746 | 0 | 0 | 0 | 16.3 | 0
747 | 0 | 0 | 0 | 15.9 | 0
748 | 0 | 0 | 0 | 15.8 | 0
749 | 0 | 0 | 0 | 15.6 | 0
750 | 58.3 | 22.2 | 84.6 | 15.3 | 0
751 | 319.4 | 97.2 | 725.1 | 15.3 | 0
752 | 583.3 | 105.6 | 892.6 | 17 | 1.67
753 | 797.2 | 127.8 | 960.2 | 20 | 2.5
754 | 936.1 | 136.1 | 992 | 23.9 | 3.89
755 | 1013.9 | 136.1 | 1005.1 | 26.2 | 3.89
756 | 1011.1 | 141.7 | 1005.1 | 27.1 | 2.44
757 | 922.2 | 141.7 | 986.7 | 27.5 | 3.89
758 | 772.2 | 136.1 | 949.8 | 27.5 | 2.78
759 | 566.7 | 133.3 | 869.8 | 27.5 | 2.22
760 | 308.3 | 97.2 | 725.1 | 27.2 | 3.33
761 | 75 | 33.3 | 84.6 | 25.2 | 3.89
762 | 0 | 0 | 0 | 23.2 | 2.78
763 | 0 | 0 | 0 | 21.1 | 2.78
764 | 0 | 0 | 0 | 19.9 | 2.78
765 | 0 | 0 | 0 | 19.2 | 1.58
766 | 0 | 0 | 0 | 18.4 | 3.33
767 | 0 | 0 | 0 | 17.4 | 2.78
768 | 0 | 0 | 0 | 16.6 | 0.56
769 | 0 | 0 | 0 | 16.4 | 2.78
770 | 0 | 0 | 0 | 15.8 | 2.78
771 | 0 | 0 | 0 | 15.9 | 1.67
772 | 0 | 0 | 0 | 15.9 | 1.67
773 | 0 | 0 | 0 | 15.5 | 1.94
774 | 44.4 | 19.4 | 89.6 | 15.3 | 1.94
775 | 305.6 | 75 | 727 | 16.7 | 1.67
776 | 583.3 | 102.8 | 893.6 | 21.2 | 2.22
777 | 802.8 | 136.1 | 960.9 | 23.1 | 3.33
778 | 955.6 | 141.7 | 992.5 | 24.5 | 3.89
779 | 1036.1 | 155.6 | 1005.6 | 25 | 3.89
780 | 1022.2 | 152.8 | 1005.6 | 25.4 | 4.44
781 | 933.3 | 152.8 | 983.9 | 26.1 | 3.33
782 | 772.2 | 144.4 | 934.4 | 26.1 | 4.44
783 | 547.2 | 122.2 | 849.9 | 26 | 3.89
784 | 308.3 | 97.2 | 727 | 25.2 | 4.44
785 | 75 | 30.6 | 89.6 | 23.8 | 3.89
786 | 0 | 0 | 0 | 22.1 | 4.44
787 | 0 | 0 | 0 | 20.5 | 3.89
788 | 0 | 0 | 0 | 19.3 | 2.78
789 | 0 | 0 | 0 | 18.8 | 2.78
790 | 0 | 0 | 0 | 18.2 | 3.33
791 | 0 | 0 | 0 | 17.5 | 2.78
792 | 0 | 0 | 0 | 16.8 | 0.83
793 | 0 | 0 | 0 | 16.3 | 3.33
794 | 0 | 0 | 0 | 15.8 | 2.22
795 | 0 | 0 | 0 | 15.7 | 1.67
796 | 0 | 0 | 0 | 14.6 | 1.67
797 | 0 | 0 | 0 | 14.4 | 1.67
798 | 30.6 | 16.7 | 94.8 | 14.5 | 1.67
799 | 211.1 | 125 | 295.7 | 15.9 | 3.33
800 | 566.7 | 72.2 | 894.5 | 18.6 | 3.33
801 | 763.9 | 161.1 | 894.4 | 21.8 | 2.78
802 | 972.2 | 197.2 | 974.1 | 23.2 | 5
803 | 1027.8 | 227.8 | 931.7 | 23.8 | 4.44
804 | 1055.6 | 211.1 | 983.5 | 25.2 | 4.44
805 | 880.6 | 219.4 | 830.9 | 25.2 | 3.89
806 | 708.3 | 258.3 | 667.7 | 25.4 | 5.56
807 | 519.4 | 188.9 | 658.6 | 24.6 | 4.44
808 | 277.8 | 111.1 | 572.3 | 24.6 | 2.78
809 | 66.7 | 33.3 | 94.8 | 23.2 | 3.89
810 | 0 | 0 | 0 | 21.5 | 3.89
811 | 0 | 0 | 0 | 20.5 | 2.78
812 | 0 | 0 | 0 | 19.6 | 3.06
813 | 0 | 0 | 0 | 19.2 | 3.33
814 | 0 | 0 | 0 | 17.5 | 3.33
815 | 0 | 0 | 0 | 17.3 | 2.78
816 | 0 | 0 | 0 | 17.2 | 1.11
817 | 0 | 0 | 0 | 17.2 | 3.33
818 | 0 | 0 | 0 | 16.7 | 2.22
819 | 0 | 0 | 0 | 15.8 | 2.78
820 | 0 | 0 | 0 | 14.9 | 2.78
821 | 0 | 0 | 0 | 14.9 | 2.22
822 | 38.9 | 13.9 | 100.1 | 14.9 | 2.78
823 | 247.2 | 102.8 | 493.3 | 15.7 | 1.67
824 | 572.2 | 150 | 838 | 17.4 | 2.78
825 | 761.1 | 163.9 | 883.3 | 20.2 | 4.44
826 | 836.1 | 275 | 703.2 | 25.58 | 5
827 | 963.9 | 288.9 | 783.9 | 23.6 | 3.89
828 | 1016.7 | 202.8 | 945.2 | 23.9 | 5
829 | 925 | 180.6 | 932.9 | 24.9 | 3.89
830 | 766.7 | 180.6 | 866.9 | 25.3 | 3.89
831 | 552.8 | 147.2 | 805 | 25.4 | 4.44
832 | 286.1 | 116.7 | 578.7 | 25.2 | 4.44
833 | 66.7 | 33.3 | 100.1 | 23.8 | 4.44
834 | 0 | 0 | 0 | 21.6 | 5
835 | 0 | 0 | 0 | 20.3 | 2.78
836 | 0 | 0 | 0 | 18.6 | 2.22
837 | 0 | 0 | 0 | 17.6 | 1.67
838 | 0 | 0 | 0 | 17.2 | 1.94
839 | 0 | 0 | 0 | 16.5 | 2.78
840 | 0 | 0 | 0 | 15.9 | 1.39
841 | 0 | 0 | 0 | 15.4 | 2.22
842 | 0 | 0 | 0 | 15.2 | 2.22
843 | 0 | 0 | 0 | 15 | 1.94
844 | 0 | 0 | 0 | 14.7 | 1.67
845 | 0 | 0 | 0 | 14.4 | 1.67
846 | 72.2 | 22.2 | 105.5 | 13.3 | 1.39
847 | 336.1 | 80.6 | 732.8 | 14.3 | 1.39
848 | 600 | 80.6 | 896.4 | 17.5 | 1.67
849 | 825 | 105.6 | 962.8 | 20.3 | 1.67
850 | 966.7 | 88.9 | 994 | 22.7 | 3.33
851 | 1033.3 | 100 | 1007 | 23.3 | 4.44
852 | 1005.6 | 108.3 | 1007 | 24.4 | 3.06
853 | 922.2 | 116.7 | 994 | 25.4 | 3.33
854 | 772.2 | 113.9 | 962.8 | 25.8 | 3.89
855 | 563.9 | 111.1 | 895.3 | 25.8 | 2.22
856 | 300 | 91.7 | 707.7 | 25.6 | 5
857 | 75 | 25 | 105.5 | 24.4 | 2.22
858 | 0 | 0 | 0 | 22.1 | 3.06
859 | 0 | 0 | 0 | 20.1 | 2.78
860 | 0 | 0 | 0 | 19.1 | 1.94
861 | 0 | 0 | 0 | 18.1 | 1.94
862 | 0 | 0 | 0 | 17.3 | 1.69
863 | 0 | 0 | 0 | 16.4 | 2.5
864 | 0 | 0 | 0 | 16.3 | 1.67
865 | 0 | 0 | 0 | 15.9 | 2.5
866 | 0 | 0 | 0 | 15.9 | 1.11
867 | 0 | 0 | 0 | 14.9 | 1.11
868 | 0 | 0 | 0 | 14.9 | 0
869 | 0 | 0 | 0 | 14.9 | 1.39
870 | 50 | 22.2 | 111.1 | 13.9 | 1.39
871 | 291.7 | 97.2 | 656.9 | 15.6 | 1.11
872 | 566.7 | 122.2 | 875.5 | 19.4 | 1.39
873 | 788.9 | 138.9 | 955.2 | 22.4 | 2.78
874 | 958.3 | 163.9 | 989.7 | 23.6 | 2.78
875 | 1025 | 186.1 | 968.7 | 24.8 | 4.44
876 | 1022.2 | 191.7 | 959.1 | 25.7 | 3.89
877 | 936.1 | 183.3 | 937.8 | 26.3 | 4.44
878 | 777.8 | 180.6 | 877.6 | 26.9 | 5
879 | 563.9 | 147.2 | 820.7 | 26.7 | 3.33
880 | 305.6 | 100 | 694.4 | 26.7 | 3.61
881 | 66.7 | 19.4 | 111.1 | 24.9 | 2.22
882 | 0 | 0 | 0 | 22.1 | 2.5
883 | 0 | 0 | 0 | 20.4 | 2.5
884 | 0 | 0 | 0 | 19.4 | 1.11
885 | 0 | 0 | 0 | 18.5 | 1.67
886 | 0 | 0 | 0 | 18.3 | 1.67
887 | 0 | 0 | 0 | 18.2 | 1.39
888 | 0 | 0 | 0 | 17.3 | 1.94
889 | 0 | 0 | 0 | 16.4 | 1.39
890 | 0 | 0 | 0 | 15.2 | 1.67
891 | 0 | 0 | 0 | 14.8 | 1.67
892 | 0 | 0 | 0 | 14.7 | 0
893 | 0 | 0 | 0 | 14.4 | 1.67
894 | 47.2 | 16.7 | 116.8 | 14.5 | 0
895 | 294.4 | 75 | 736.7 | 15.3 | 0
896 | 583.3 | 102.8 | 898.3 | 19.9 | 0
897 | 802.8 | 108.3 | 964.1 | 22.1 | 1.67
898 | 944.4 | 119.4 | 995.1 | 23.6 | 3.06
899 | 1033.3 | 138.9 | 1007.9 | 25 | 4.44
900 | 1058.3 | 136.1 | 1007.9 | 26.2 | 3.89
901 | 966.7 | 125 | 995.1 | 26.8 | 2.78
902 | 797.2 | 130.6 | 964.1 | 27.4 | 1.11
903 | 572.2 | 119.4 | 888.4 | 27.2 | 2.78
904 | 302.8 | 88.9 | 718.6 | 26.9 | 1.67
905 | 66.7 | 33.3 | 116.8 | 25.6 | 1.94
906 | 0 | 0 | 0 | 23.3 | 1.39
907 | 0 | 0 | 0 | 22.2 | 0.56
908 | 0 | 0 | 0 | 21.8 | 0.56
909 | 0 | 0 | 0 | 18.8 | 0.56
910 | 0 | 0 | 0 | 17.5 | 2.22
911 | 0 | 0 | 0 | 17 | 1.67
912 | 0 | 0 | 0 | 16.9 | 2.22
913 | 0 | 0 | 0 | 16.7 | 2.22
914 | 0 | 0 | 0 | 16.2 | 1.67
915 | 0 | 0 | 0 | 15.7 | 1.67
916 | 0 | 0 | 0 | 15.1 | 0.56
917 | 0 | 0 | 0 | 14.8 | 0
918 | 77.8 | 11.1 | 122.6 | 15 | 0
919 | 325 | 75 | 738.6 | 16.1 | 0
920 | 586.1 | 116.7 | 899.3 | 21.3 | 0
921 | 775 | 147.2 | 916.6 | 24.6 | 0
922 | 941.7 | 138.9 | 994.2 | 26.3 | 0.56
923 | 1011.1 | 158.3 | 979.1 | 27.2 | 1.39
924 | 1011.1 | 166.7 | 969.6 | 28.1 | 1.67
925 | 938.9 | 155.6 | 970.1 | 29.2 | 1.11
926 | 786.1 | 141.7 | 940.9 | 28.9 | 1.67
927 | 572.2 | 133.3 | 857.9 | 28.6 | 2.78
928 | 302.8 | 88.9 | 714.6 | 28.2 | 2.5
929 | 66.7 | 25 | 122.6 | 27.3 | 2.78
930 | 0 | 0 | 0 | 25.6 | 2.22
931 | 0 | 0 | 0 | 23.9 | 1.67
932 | 0 | 0 | 0 | 21.7 | 1.67
933 | 0 | 0 | 0 | 20.7 | 1.39
934 | 0 | 0 | 0 | 20.2 | 1.39
935 | 0 | 0 | 0 | 19.3 | 1.67
936 | 0 | 0 | 0 | 18 | 2.5
937 | 0 | 0 | 0 | 17 | 2.22
938 | 0 | 0 | 0 | 15.7 | 2.22
939 | 0 | 0 | 0 | 15.4 | 0.83
940 | 0 | 0 | 0 | 14.1 | 0
941 | 0 | 0 | 0 | 13.6 | 0
942 | 50 | 22.2 | 128.5 | 13.1 | 0
943 | 294.4 | 80.6 | 710.6 | 13.5 | 0
944 | 594.4 | 69.4 | 900.3 | 19.5 | 0
945 | 813.9 | 77.8 | 965.4 | 22.8 | 0.83
946 | 966.7 | 97.2 | 996.1 | 25.3 | 2.22
947 | 1036.1 | 116.7 | 1008.9 | 27.8 | 1.67
948 | 1033.3 | 122.2 | 1008.9 | 28.4 | 3.33
949 | 941.7 | 136.1 | 994.6 | 29.2 | 3.89
950 | 775 | 138.9 | 925.7 | 29.5 | 2.78
951 | 555.6 | 127.8 | 832.9 | 30.1 | 1.67
952 | 280.6 | 80.6 | 664.5 | 29.7 | 2.5
953 | 55.6 | 25 | 128.5 | 28 | 2.5
954 | 0 | 0 | 0 | 24.9 | 2.5
955 | 0 | 0 | 0 | 22.7 | 2.78
956 | 0 | 0 | 0 | 21.5 | 2.78
957 | 0 | 0 | 0 | 20.7 | 1.39
958 | 0 | 0 | 0 | 19.3 | 1.67
959 | 0 | 0 | 0 | 17.9 | 1.67
960 | 0 | 0 | 0 | 17.6 | 2.78
961 | 0 | 0 | 0 | 16.7 | 2.78
962 | 0 | 0 | 0 | 15.6 | 2.22
963 | 0 | 0 | 0 | 14.8 | 1.11
964 | 0 | 0 | 0 | 14.5 | 1.11
965 | 0 | 0 | 0 | 14.4 | 1.11
966 | 22.2 | 13.9 | 127.8 | 14.6 | 1.11
967 | 127.8 | 105.6 | 73.4 | 15.1 | 1.11
968 | 530.6 | 125 | 786.6 | 18.7 | 1.39
969 | 822.2 | 122.2 | 966.1 | 21.2 | 2.78
970 | 697.2 | 130.6 | 697.6 | 23.5 | 2.5
971 | 1033.3 | 161.1 | 995.7 | 25.2 | 2.22
972 | 972.2 | 163.9 | 922.8 | 25.7 | 4.44
973 | 933.3 | 183.3 | 923.2 | 26.5 | 2.78
974 | 775 | 180.6 | 862.2 | 27.2 | 2.78
975 | 547.2 | 141.7 | 786.6 | 27.9 | 2.22
976 | 275 | 97.2 | 587.3 | 27.7 | 2.22
977 | 63.9 | 30.6 | 134.6 | 26.1 | 1.67
978 | 0 | 0 | 0 | 23.2 | 2.78
979 | 0 | 0 | 0 | 22.2 | 1.11
980 | 0 | 0 | 0 | 21.7 | 1.67
981 | 0 | 0 | 0 | 19.8 | 2.78
982 | 0 | 0 | 0 | 19.4 | 1.67
983 | 0 | 0 | 0 | 18.6 | 2.22
984 | 0 | 0 | 0 | 18.6 | 3.06
985 | 0 | 0 | 0 | 17.3 | 2.22
986 | 0 | 0 | 0 | 16.7 | 2.78
987 | 0 | 0 | 0 | 16.2 | 2.22
988 | 0 | 0 | 0 | 15.9 | 1.11
989 | 0 | 0 | 0 | 15.1 | 2.22
990 | 58.3 | 38.9 | 140.7 | 14.7 | 0
991 | 294.4 | 125 | 556.7 | 15.2 | 0
992 | 588.9 | 116.7 | 902.2 | 19.5 | 0
993 | 819.4 | 141.7 | 966.7 | 22.5 | 1.11
994 | 961.1 | 150 | 995.5 | 24.1 | 1.67
995 | 1038.9 | 169.4 | 989.7 | 25.2 | 1.67
996 | 1030.6 | 138.9 | 1009.8 | 26.2 | 1.67
997 | 950 | 141.7 | 992.1 | 26.7 | 2.78
998 | 800 | 138.9 | 955.8 | 27.4 | 2.22
999 | 580.6 | 108.3 | 902.2 | 27.8 | 1.67
1000 | 300 | 75 | 739.2 | 27.7 | 2.22
1001 | 61.1 | 13.9 | 140.7 | 26 | 2.22
1002 | 0 | 0 | 0 | 23.6 | 2.22
1003 | 0 | 0 | 0 | 22.7 | 1.11
1004 | 0 | 0 | 0 | 21.8 | 1.94
1005 | 0 | 0 | 0 | 20.6 | 1.67
1006 | 0 | 0 | 0 | 19.7 | 0.83
1007 | 0 | 0 | 0 | 19 | 1.11
1008 | 0 | 0 | 0 | 19 | 3.33
1009 | 0 | 0 | 0 | 18.9 | 3.89
1010 | 0 | 0 | 0 | 18.5 | 2.22
1011 | 0 | 0 | 0 | 18.2 | 2.22
1012 | 0 | 0 | 0 | 17.6 | 2.78
1013 | 0 | 0 | 0 | 17.3 | 1.67
1014 | 69.4 | 22.2 | 147 | 16.6 | 1.67
1015 | 333.3 | 69.4 | 746.4 | 17.4 | 0
1016 | 608.3 | 66.7 | 903.2 | 20 | 1.67
1017 | 825 | 113.9 | 967.4 | 21.8 | 1.67
1018 | 802.8 | 163.9 | 781.8 | 23.8 | 2.22
1019 | 852.8 | 225 | 712.5 | 25.8 | 2.22
1020 | 725 | 283.3 | 501.3 | 25.8 | 2.22
1021 | 625 | 250 | 458.9 | 26.9 | 2.78
1022 | 508.3 | 225 | 408.3 | 26.8 | 1.67
1023 | 508.3 | 172.2 | 646.8 | 26.5 | 2.22
1024 | 322.2 | 80.6 | 746.4 | 26.5 | 2.22
1025 | 69.4 | 13.9 | 147 | 25.2 | 2.22
1026 | 0 | 0 | 0 | 22.7 | 2.78
1027 | 0 | 0 | 0 | 21.4 | 1.11
1028 | 0 | 0 | 0 | 20.6 | 0.83
1029 | 0 | 0 | 0 | 20.4 | 1.67
1030 | 0 | 0 | 0 | 20.1 | 1.94
1031 | 0 | 0 | 0 | 19.4 | 1.94
1032 | 0 | 0 | 0 | 19.3 | 3.61
1033 | 0 | 0 | 0 | 18.8 | 1.67
1034 | 0 | 0 | 0 | 18.1 | 2.78
1035 | 0 | 0 | 0 | 17.7 | 1.67
1036 | 0 | 0 | 0 | 16.9 | 1.67
1037 | 0 | 0 | 0 | 16.4 | 1.67
1038 | 38.9 | 19.4 | 153.3 | 16.4 | 0.56
1039 | 225 | 113.9 | 360.9 | 16.4 | 1.11
1040 | 586.1 | 125 | 883.9 | 19 | 1.67
1041 | 836.1 | 105.6 | 968 | 21 | 1.11
1042 | 983.3 | 111.1 | 998.2 | 23.5 | 0.28
1043 | 1052.8 | 130.6 | 1010.8 | 25.4 | 1.11
1044 | 1047.2 | 116.7 | 1010.8 | 26.3 | 0.83
1045 | 963.9 | 113.9 | 998.2 | 27 | 1.11
1046 | 791.7 | 113.9 | 968 | 27.5 | 1.11
1047 | 552.8 | 108.3 | 852 | 27.7 | 2.22
1048 | 291.7 | 80.6 | 685.7 | 27.6 | 0.56
1049 | 69.4 | 22.2 | 153.3 | 27.2 | 1.39
1050 | 0 | 0 | 0 | 25.1 | 1.39
1051 | 0 | 0 | 0 | 22.8 | 0.56
1052 | 0 | 0 | 0 | 21.7 | 1.39
1053 | 0 | 0 | 0 | 20.9 | 2.78
1054 | 0 | 0 | 0 | 20.6 | 1.94
1055 | 0 | 0 | 0 | 20 | 1.94
1056 | 0 | 0 | 0 | 18.9 | 3.89
1057 | 0 | 0 | 0 | 18.5 | 2.22
1058 | 0 | 0 | 0 | 17.8 | 2.22
1059 | 0 | 0 | 0 | 17.7 | 1.39
1060 | 0 | 0 | 0 | 17.4 | 1.39
1061 | 0 | 0 | 0 | 16.6 | 1.39
1062 | 66.7 | 16.7 | 159.7 | 16.6 | 0.56
1063 | 350 | 77.8 | 750.3 | 17.8 | 0.56
1064 | 627.8 | 69.4 | 905.1 | 21.6 | 1.67
1065 | 841.7 | 72.2 | 968.7 | 24.9 | 0
1066 | 980.6 | 100 | 998.7 | 25.9 | 0.56
1067 | 1050 | 111.1 | 1011.3 | 27.3 | 0.28
1068 | 1025 | 119.4 | 1011.3 | 28.3 | 1.11
1069 | 938.9 | 122.2 | 993.3 | 29.3 | 0.83
1070 | 783.3 | 122.2 | 946.4 | 29.8 | 0.83
1071 | 566.7 | 105.6 | 880.4 | 30.3 | 1.39
1072 | 316.7 | 80.6 | 750.3 | 30.3 | 1.11
1073 | 50 | 19.4 | 159.7 | 29.2 | 1.11
1074 | 0 | 0 | 0 | 27.1 | 0
1075 | 0 | 0 | 0 | 25.1 | 0
1076 | 0 | 0 | 0 | 23 | 0
1077 | 0 | 0 | 0 | 21.7 | 1.67
1078 | 0 | 0 | 0 | 21.2 | 0.56
1079 | 0 | 0 | 0 | 20.6 | 0.83
1080 | 0 | 0 | 0 | 20.6 | 4.17
1081 | 0 | 0 | 0 | 19.7 | 0.56
1082 | 0 | 0 | 0 | 19.3 | 1.67
1083 | 0 | 0 | 0 | 19.2 | 1.11
1084 | 0 | 0 | 0 | 18.3 | 1.11
1085 | 0 | 0 | 0 | 18.1 | 1.11
1086 | 51.4 | 16.7 | 160.1 | 17.4 | 1.11
1087 | 280 | 80.6 | 591.6 | 19.4 | 0
1088 | 586.1 | 100 | 906.1 | 23 | 0.56
1089 | 819.4 | 100 | 969.3 | 25.5 | 0
1090 | 963.9 | 122.2 | 999.2 | 27.8 | 1.11
1091 | 1036.1 | 138.9 | 1009.6 | 28.9 | 1.67
1092 | 1025 | 152.8 | 981.4 | 29.6 | 2.22
1093 | 944.4 | 158.3 | 953.3 | 30.2 | 1.67
1094 | 780.6 | 161.1 | 883.9 | 30.8 | 2.78
1095 | 588.9 | 141.7 | 850.6 | 30.4 | 1.67
1096 | 163.9 | 130.6 | 107.1 | 30.2 | 1.67
1097 | 38.9 | 50 | 0 | 29.3 | 2.78
1098 | 0 | 0 | 0 | 27.9 | 0.56
1099 | 0 | 0 | 0 | 26.8 | 0.56
1100 | 0 | 0 | 0 | 24.6 | 0.56
1101 | 0 | 0 | 0 | 23 | 1.67
1102 | 0 | 0 | 0 | 22.2 | 1.67
1103 | 0 | 0 | 0 | 21.4 | 1.67
1104 | 0 | 0 | 0 | 20.8 | 4.44
1105 | 0 | 0 | 0 | 20.4 | 1.67
1106 | 0 | 0 | 0 | 19.2 | 1.67
1107 | 0 | 0 | 0 | 19.3 | 1.11
1108 | 0 | 0 | 0 | 19.3 | 1.39
1109 | 0 | 0 | 0 | 18.7 | 1.39
1110 | 50 | 25 | 172.7 | 18.8 | 1.39
1111 | 297.2 | 88.9 | 665.3 | 20.2 | 1.39
1112 | 547.2 | 105.6 | 836.7 | 24.3 | 1.11
1113 | 750 | 133.3 | 877 | 26.5 | 2.22
1114 | 850 | 158.3 | 836.2 | 27.6 | 2.22
1115 | 927.8 | 227.8 | 785.4 | 28.5 | 2.22
1116 | 630.6 | 344.4 | 321 | 29.8 | 1.39
1117 | 819.4 | 263.9 | 671.7 | 30.5 | 2.22
1118 | 694.4 | 219.4 | 675.5 | 30.5 | 2.78
1119 | 511.1 | 175 | 636.8 | 30.6 | 1.67
1120 | 266.7 | 83.3 | 585.5 | 30.5 | 2.78
1121 | 44.4 | 16.7 | 172.7 | 29.9 | 1.67
1122 | 0 | 0 | 0 | 28 | 1.11
1123 | 0 | 0 | 0 | 26.6 | 1.49
1124 | 0 | 0 | 0 | 25.8 | 1.11
1125 | 0 | 0 | 0 | 25.2 | 0.28
1126 | 0 | 0 | 0 | 23.9 | 0.28
1127 | 0 | 0 | 0 | 22 | 1.67
1128 | 0 | 0 | 0 | 21.5 | 4.72
1129 | 0 | 0 | 0 | 21 | 1.39
1130 | 0 | 0 | 0 | 20.6 | 0.56
1131 | 0 | 0 | 0 | 20.2 | 0.56
1132 | 0 | 0 | 0 | 19.9 | 0.83
1133 | 0 | 0 | 0 | 19.4 | 0.56
1134 | 47.2 | 8.3 | 179.3 | 19.4 | 1.39
1135 | 286.1 | 61.1 | 714.5 | 21.1 | 1.39
1136 | 547.2 | 75 | 891.1 | 24.7 | 0
1137 | 800 | 88.9 | 970.6 | 27.7 | 1.94
1138 | 963.9 | 113.9 | 1000.3 | 29.2 | 2.78
1139 | 1038.9 | 116.7 | 1012.6 | 30 | 3.33
1140 | 1036.1 | 111.1 | 1012.6 | 31.3 | 3.89
1141 | 950 | 113.9 | 1000.3 | 31.7 | 2.5
1142 | 783.3 | 116.7 | 945 | 31.9 | 2.22
1143 | 572.2 | 97.2 | 896.4 | 31.7 | 2.22
1144 | 322.2 | 86.1 | 749.8 | 31.2 | 1.39
1145 | 61.1 | 36.1 | 179.3 | 30.6 | 1.67
1146 | 0 | 0 | 0 | 28.7 | 0.56
1147 | 0 | 0 | 0 | 27.4 | 0.56
1148 | 0 | 0 | 0 | 26.3 | 1.11
1149 | 0 | 0 | 0 | 25.3 | 1.67
1150 | 0 | 0 | 0 | 22 | 2.5
1151 | 0 | 0 | 0 | 20.5 | 2.5
1152 | 0 | 0 | 0 | 20.7 | 5
1153 | 0 | 0 | 0 | 19.9 | 4.44
1154 | 0 | 0 | 0 | 19.9 | 2.78
1155 | 0 | 0 | 0 | 19.7 | 1.11
1156 | 0 | 0 | 0 | 19.8 | 1.11
1157 | 0 | 0 | 0 | 18.8 | 0
1158 | 55.6 | 25 | 185.9 | 18.8 | 0
1159 | 308.3 | 102.8 | 649 | 19.7 | 0
1160 | 555.6 | 111.1 | 835.5 | 23.7 | 0
1161 | 772.2 | 113.9 | 930.2 | 27.9 | 2.22
1162 | 925 | 130.6 | 954.8 | 29.5 | 2.22
1163 | 1011.1 | 136.1 | 976.1 | 31 | 1.67
1164 | 997.2 | 136.1 | 960.7 | 32 | 1.67
1165 | 902.8 | 136.1 | 921.4 | 32.1 | 1.11
1166 | 758.3 | 133.3 | 883.1 | 32.2 | 1.11
1167 | 547.2 | 119.4 | 804.1 | 31.8 | 1.11
1168 | 286.1 | 86.1 | 631.5 | 31.5 | 1.67
1169 | 77.8 | 30.6 | 185.9 | 30.4 | 2.22
1170 | 0 | 0 | 0 | 28.4 | 0
1171 | 0 | 0 | 0 | 26.8 | 0
1172 | 0 | 0 | 0 | 25.6 | 0
1173 | 0 | 0 | 0 | 24 | 0.56
1174 | 0 | 0 | 0 | 21.9 | 0
1175 | 0 | 0 | 0 | 19.3 | 0.56
1176 | 0 | 0 | 0 | 20.3 | 5.28
1177 | 0 | 0 | 0 | 20.4 | 0
1178 | 0 | 0 | 0 | 18.6 | 0
1179 | 0 | 0 | 0 | 19.4 | 0.56
1180 | 0 | 0 | 0 | 19.1 | 1.39
1181 | 0 | 0 | 0 | 18.9 | 0
1182 | 63.9 | 38.9 | 192.6 | 18.8 | 0
1183 | 300 | 97.2 | 636.7 | 20.4 | 0
1184 | 563.9 | 97.2 | 873.8 | 24.7 | 0
1185 | 761.1 | 119.4 | 903.7 | 27.5 | 1.39
1186 | 919.4 | 138.9 | 935.3 | 29.1 | 2.22
1187 | 1002.8 | 144.4 | 954.8 | 30.6 | 1.67
1188 | 988.9 | 144.4 | 939.4 | 31.4 | 2.22
1189 | 916.7 | 150 | 918.7 | 31.4 | 2.22
1190 | 766.7 | 138.9 | 884.1 | 31.6 | 1.11
1191 | 544.4 | 144.4 | 749 | 32.1 | 2.22
1192 | 277.8 | 86.1 | 601.8 | 31.8 | 1.67
1193 | 44.4 | 19.4 | 192.6 | 31 | 0.28
1194 | 0 | 0 | 0 | 29.4 | 0.28
1195 | 0 | 0 | 0 | 28.4 | 0.56
1196 | 0 | 0 | 0 | 25 | 0.28
1197 | 0 | 0 | 0 | 25 | 0
1198 | 0 | 0 | 0 | 23.5 | 0
1199 | 0 | 0 | 0 | 23.1 | 0
1200 | 0 | 0 | 0 | 21.6 | 5.56
1201 | 0 | 0 | 0 | 21.6 | 1.11
1202 | 0 | 0 | 0 | 21 | 0.28
1203 | 0 | 0 | 0 | 20.1 | 0.28
1204 | 0 | 0 | 0 | 19.6 | 0.56
1205 | 0 | 0 | 0 | 19.6 | 0.83
1206 | 66.7 | 30.6 | 199.3 | 19.4 | 0.83
1207 | 330.6 | 97.2 | 728.5 | 20 | 0.56
1208 | 580.6 | 102.8 | 891.2 | 23 | 0
1209 | 791.7 | 111.1 | 955.4 | 25.5 | 1.39
1210 | 938.9 | 122.2 | 975.7 | 28.4 | 1.67
1211 | 1019.4 | 138.9 | 976.8 | 29.5 | 2.22
1212 | 1002.8 | 147.2 | 949.1 | 30.7 | 2.22
1213 | 922.2 | 147.2 | 926 | 31 | 2.22
1214 | 772.2 | 141.7 | 885.2 | 31.3 | 2.78
1215 | 558.3 | 125 | 808.3 | 31.3 | 2.78
1216 | 294.4 | 86.1 | 650.4 | 31.2 | 2.5
1217 | 61.1 | 25 | 199.3 | 30.9 | 1.11
1218 | 0 | 0 | 0 | 29 | 1.67
1219 | 0 | 0 | 0 | 26.9 | 1.67
1220 | 0 | 0 | 0 | 24.8 | 0
1221 | 0 | 0 | 0 | 23.1 | 0
1222 | 0 | 0 | 0 | 23.4 | 1.94
1223 | 0 | 0 | 0 | 22.9 | 1.94
1224 | 0 | 0 | 0 | 22.4 | 5.83
1225 | 0 | 0 | 0 | 21.4 | 1.11
1226 | 0 | 0 | 0 | 21.4 | 0
1227 | 0 | 0 | 0 | 20.9 | 1.67
1228 | 0 | 0 | 0 | 20.8 | 1.67
1229 | 0 | 0 | 0 | 20.5 | 1.39
1230 | 47.2 | 13.9 | 206 | 19.9 | 1.39
1231 | 297.2 | 116.7 | 560.5 | 21 | 0
1232 | 605.6 | 144.4 | 856.8 | 23.8 | 1.11
1233 | 813.9 | 177.8 | 890.1 | 26 | 3.33
1234 | 969.4 | 186.1 | 933.2 | 27 | 3.33
1235 | 1038.9 | 191.7 | 937.2 | 28 | 2.22
1236 | 1030.6 | 172.2 | 949.5 | 29.2 | 2.22
1237 | 925 | 183.3 | 883.6 | 30.1 | 2.78
1238 | 808.3 | 155.6 | 913.4 | 30.2 | 1.67
1239 | 591.7 | 136.1 | 846.4 | 30.3 | 2.22
1240 | 341.7 | 100 | 750.3 | 30.5 | 1.67
1241 | 77.8 | 41.7 | 206 | 29.3 | 1.11
1242 | 0 | 0 | 0 | 28.1 | 1.67
1243 | 0 | 0 | 0 | 26.5 | 1.67
1244 | 0 | 0 | 0 | 26.2 | 1.67
1245 | 0 | 0 | 0 | 23.2 | 1.67
1246 | 0 | 0 | 0 | 22 | 1.67
1247 | 0 | 0 | 0 | 21.8 | 0.83
1248 | 0 | 0 | 0 | 21.5 | 6.11
1249 | 0 | 0 | 0 | 21 | 1.39
1250 | 0 | 0 | 0 | 20.5 | 2.22
1251 | 0 | 0 | 0 | 19 | 1.11
1252 | 0 | 0 | 0 | 18.9 | 0
1253 | 0 | 0 | 0 | 18.8 | 1.39
1254 | 69.4 | 22.2 | 212.7 | 18.5 | 1.11
1255 | 333.3 | 122.2 | 651.7 | 19 | 0
1256 | 633.3 | 102.8 | 912.7 | 22.9 | 1.67
1257 | 858.3 | 111.1 | 973.7 | 25.8 | 0
1258 | 1002.8 | 113.9 | 1002.8 | 27.7 | 1.11
1259 | 1066.7 | 150 | 1011.2 | 28.3 | 2.22
1260 | 1036.1 | 147.2 | 980.6 | 29.5 | 2.22
1261 | 947.2 | 147.2 | 950.3 | 29.9 | 1.67
1262 | 786.1 | 147.2 | 891.1 | 30.5 | 0
1263 | 588.9 | 127.8 | 853.5 | 30.5 | 2.22
1264 | 411.1 | 88.9 | 765.7 | 30.1 | 1.39
1265 | 69.4 | 22.2 | 212.7 | 29.4 | 0
1266 | 0 | 0 | 0 | 27.5 | 1.11
1267 | 0 | 0 | 0 | 26.4 | 0
1268 | 0 | 0 | 0 | 24.5 | 2.22
1269 | 0 | 0 | 0 | 23.8 | 0.56
1270 | 0 | 0 | 0 | 23 | 0.56
1271 | 0 | 0 | 0 | 22.2 | 1.11
1272 | 0 | 0 | 0 | 21.6 | 6.39
1273 | 0 | 0 | 0 | 21.5 | 1.11
1274 | 0 | 0 | 0 | 21.2 | 1.67
1275 | 0 | 0 | 0 | 21 | 1.67
1276 | 0 | 0 | 0 | 20 | 1.39
1277 | 0 | 0 | 0 | 19.4 | 1.11
1278 | 50 | 22.2 | 219.5 | 18.6 | 0
1279 | 286.1 | 97.2 | 579.9 | 19.5 | 0
1280 | 563.9 | 141.7 | 778.5 | 22.2 | 0
1281 | 783.3 | 163.9 | 861.3 | 24.4 | 0.83
1282 | 933.3 | 247.2 | 812.7 | 26.2 | 1.11
1283 | 669.4 | 322.2 | 382 | 27.6 | 1.11
1284 | 638.9 | 322.2 | 348.4 | 29 | 1.67
1285 | 733.3 | 313.9 | 496.8 | 29.3 | 1.67
1286 | 472.2 | 252.8 | 305.1 | 29.8 | 2.22
1287 | 486.1 | 197.2 | 532.7 | 29.7 | 1.67
1288 | 258.3 | 125 | 409.3 | 29.2 | 1.11
1289 | 55.6 | 38.9 | 198.1 | 28.7 | 0.83
1290 | 0 | 0 | 0 | 27.2 | 0.56
1291 | 0 | 0 | 0 | 25.9 | 0
1292 | 0 | 0 | 0 | 24.6 | 1.11
1293 | 0 | 0 | 0 | 22.9 | 2.78
1294 | 0 | 0 | 0 | 21.7 | 1.67
1295 | 0 | 0 | 0 | 20.5 | 1.67
1296 | 0 | 0 | 0 | 19.8 | 6.67
1297 | 0 | 0 | 0 | 19.7 | 2.22
1298 | 0 | 0 | 0 | 19.7 | 1.39
1299 | 0 | 0 | 0 | 18.9 | 1.39
1300 | 0 | 0 | 0 | 18.3 | 1.39
1301 | 0 | 0 | 0 | 17.9 | 1.11
1302 | 36.1 | 11.1 | 226.3 | 17.7 | 0.83
1303 | 286.1 | 102.8 | 559.7 | 17.9 | 1.11
1304 | 527.8 | 147.2 | 699 | 20.7 | 0
1305 | 538.9 | 161.1 | 523.6 | 23.3 | 0.56
1306 | 952.8 | 200 | 889.1 | 25.7 | 1.67
1307 | 977.8 | 222.2 | 828.9 | 27.3 | 1.67
1308 | 1011.1 | 197.2 | 892.9 | 28.2 | 1.67
1309 | 897.2 | 186.1 | 839.9 | 29.2 | 2.22
1310 | 744.9 | 186.1 | 852.5 | 29.2 | 2.22
1311 | 544.5 | 177.8 | 794.3 | 29.2 | 2.22
1312 | 287.6 | 108.3 | 630.8 | 29.1 | 1.67
1313 | 61.1 | 30.6 | 145.6 | 27.5 | 1.67
1314 | 0 | 0 | 0 | 25 | 1.67
1315 | 0 | 0 | 0 | 23.6 | 2.78
1316 | 0 | 0 | 0 | 22.7 | 2.22
1317 | 0 | 0 | 0 | 22.2 | 1.11
1318 | 0 | 0 | 0 | 21.8 | 2.78
1319 | 0 | 0 | 0 | 20.7 | 2.22
1320 | 0 | 0 | 0 | 19.7 | 6.94
1321 | 0 | 0 | 0 | 18.7 | 1.67
1322 | 0 | 0 | 0 | 18.1 | 1.67
1323 | 0 | 0 | 0 | 17.5 | 2.22
1324 | 0 | 0 | 0 | 16.8 | 0.83
1325 | 0 | 0 | 0 | 16.3 | 0.56
1326 | 33.3 | 16.7 | 191.1 | 16.2 | 0
1327 | 205.6 | 83.3 | 371.1 | 16.3 | 0
1328 | 538.9 | 138.9 | 731.9 | 16.1 | 0.28
1329 | 788.9 | 133.3 | 905.8 | 19.6 | 1.11
1330 | 936.1 | 127.8 | 952 | 23.3 | 0.56
1331 | 1022.2 | 119.4 | 987.7 | 26.2 | 1.67
1332 | 1025 | 127.8 | 981.7 | 28 | 1.67
1333 | 922.2 | 125 | 938.9 | 29.2 | 2.22
1334 | 763.9 | 122.2 | 886.6 | 29.3 | 1.67
1335 | 558.3 | 113.9 | 813.3 | 29.3 | 1.11
1336 | 297.2 | 75 | 674.7 | 29 | 1.11
1337 | 41.7 | 30.6 | 127.4 | 27.1 | 0.56
1338 | 0 | 0 | 0 | 24.7 | 1.67
1339 | 0 | 0 | 0 | 23.7 | 1.67
1340 | 0 | 0 | 0 | 22.4 | 1.67
1341 | 0 | 0 | 0 | 21.7 | 1.11
1342 | 0 | 0 | 0 | 20.4 | 1.67
1343 | 0 | 0 | 0 | 19.9 | 1.67
1344 | 0 | 0 | 0 | 19.4 | 7.22
1345 | 0 | 0 | 0 | 19.2 | 1.67
1346 | 0 | 0 | 0 | 19.1 | 1.67
1347 | 0 | 0 | 0 | 18.6 | 2.22
1348 | 0 | 0 | 0 | 18.1 | 2.22
1349 | 0 | 0 | 0 | 17.2 | 1.67
1350 | 36.1 | 22.2 | 156.4 | 17 | 0.56
1351 | 208.3 | 94.4 | 343.9 | 17.3 | 0
1352 | 572.2 | 113.9 | 835.5 | 18.8 | 0
1353 | 783.3 | 119.4 | 914.4 | 22 | 0
1354 | 950 | 102.8 | 995 | 24.3 | 0.56
1355 | 1033.3 | 75 | 1016.6 | 26 | 1.39
1356 | 1027.8 | 63.9 | 1016.6 | 27.5 | 0.56
1357 | 958.3 | 72.2 | 1004.7 | 27.8 | 2.78
1358 | 797.2 | 86.1 | 976.1 | 28.3 | 1.11
1359 | 577.8 | 108.3 | 855.8 | 28.3 | 2.22
1360 | 322.2 | 100 | 671 | 28 | 2.22
1361 | 75 | 36.1 | 239.8 | 27 | 1.11
1362 | 0 | 0 | 0 | 24.6 | 1.11
1363 | 0 | 0 | 0 | 23.3 | 1.11
1364 | 0 | 0 | 0 | 22.5 | 1.67
1365 | 0 | 0 | 0 | 21.8 | 1.67
1366 | 0 | 0 | 0 | 21.4 | 1.11
1367 | 0 | 0 | 0 | 20.9 | 2.22
1368 | 0 | 0 | 0 | 20.3 | 7.5
1369 | 0 | 0 | 0 | 19.7 | 1.67
1370 | 0 | 0 | 0 | 18.8 | 1.67
1371 | 0 | 0 | 0 | 18.8 | 1.11
1372 | 0 | 0 | 0 | 18.4 | 1.39
1373 | 0 | 0 | 0 | 18.4 | 0.83
1374 | 52.8 | 30.6 | 246 | 18.5 | 0.56
1375 | 311.1 | 105.6 | 617.2 | 19.2 | 1.39
1376 | 569.4 | 155.6 | 751.7 | 21.1 | 1.11
1377 | 769.4 | 191.7 | 793.4 | 23.5 | 1.67
1378 | 905.6 | 222.2 | 800.3 | 25.6 | 1.67
1379 | 966.7 | 244.4 | 786 | 27.1 | 1.11
1380 | 994.4 | 216.7 | 846.4 | 28.6 | 1.11
1381 | 758.3 | 230.6 | 618.1 | 28.8 | 1.67
1382 | 772.2 | 186.1 | 804.8 | 29.6 | 1.11
1383 | 433.3 | 180.6 | 459.1 | 29.3 | 2.22
1384 | 191.7 | 127.8 | 191.8 | 29.2 | 1.11
1385 | 50 | 41.7 | 92.2 | 28.6 | 0.56
1386 | 0 | 0 | 0 | 26.1 | 0
1387 | 0 | 0 | 0 | 24.7 | 1.67
1388 | 0 | 0 | 0 | 24.1 | 1.11
1389 | 0 | 0 | 0 | 23 | 2.78
1390 | 0 | 0 | 0 | 22.2 | 1.11
1391 | 0 | 0 | 0 | 21.5 | 1.67
1392 | 0 | 0 | 0 | 20.8 | 7.78
1393 | 0 | 0 | 0 | 20.2 | 2.22
1394 | 0 | 0 | 0 | 19.8 | 0.28
1395 | 0 | 0 | 0 | 19.5 | 0
1396 | 0 | 0 | 0 | 19.4 | 0.83
1397 | 0 | 0 | 0 | 18.8 | 1.39
1398 | 55.6 | 27.8 | 253.3 | 19.1 | 1.67
1399 | 155.6 | 94.4 | 591.6 | 20.4 | 1.11
1400 | 466.7 | 109.7 | 858.1 | 21.9 | 3.89
1401 | 688.9 | 127.7 | 917.3 | 24.4 | 3.89
1402 | 750 | 148.1 | 932.9 | 25.4 | 3.89
1403 | 894.4 | 167.9 | 929 | 26.6 | 2.78
1404 | 430.6 | 168.1 | 908.5 | 27.6 | 1.11
1405 | 313.9 | 164.8 | 893.2 | 28.3 | 1.11
1406 | 569.4 | 157.5 | 852.5 | 28.2 | 1.11
1407 | 375 | 137.4 | 794.3 | 27.7 | 1.67
1408 | 152.8 | 95.2 | 630.8 | 27.2 | 1.67
1409 | 25 | 16.7 | 90.7 | 27.2 | 0.56
1410 | 0 | 0 | 0 | 25.7 | 0
1411 | 0 | 0 | 0 | 24.7 | 1.67
1412 | 0 | 0 | 0 | 24.6 | 1.11
1413 | 0 | 0 | 0 | 19.3 | 1.67
1414 | 0 | 0 | 0 | 19.4 | 2.78
1415 | 0 | 0 | 0 | 19.6 | 1.67
1416 | 0 | 0 | 0 | 20.1 | 0.28
1417 | 0 | 0 | 0 | 19.4 | 0
1418 | 0 | 0 | 0 | 19.1 | 1.11
1419 | 0 | 0 | 0 | 18.4 | 1.94
1420 | 0 | 0 | 0 | 17.8 | 1.11
1421 | 0 | 0 | 0 | 17.9 | 0
1422 | 52.8 | 25 | 236.5 | 17.9 | 1.11
1423 | 222.2 | 91.9 | 570.6 | 20 | 1.11
1424 | 444.4 | 136.5 | 652.7 | 22.8 | 1.39
1425 | 669.4 | 172.2 | 678.6 | 24.4 | 1.67
1426 | 830.6 | 188.9 | 747.4 | 26 | 2.5
1427 | 894.4 | 261.1 | 685.7 | 27.7 | 2.5
1428 | 930.6 | 173.5 | 769.9 | 29.8 | 2.5
1429 | 444.4 | 164.5 | 756.1 | 30 | 4.44
1430 | 608.3 | 294.4 | 428.4 | 30.2 | 3.89
1431 | 563.9 | 277.8 | 515.8 | 30.5 | 2.22
1432 | 294.4 | 158.3 | 404.3 | 29.9 | 4.44
1433 | 63.9 | 44.4 | 208 | 27.9 | 3.33
1434 | 0 | 0 | 0 | 25.5 | 3.33
1435 | 0 | 0 | 0 | 24 | 3.33
1436 | 0 | 0 | 0 | 22.5 | 3.33
1437 | 0 | 0 | 0 | 21.8 | 3.33
1438 | 0 | 0 | 0 | 20.8 | 3.06
1439 | 0 | 0 | 0 | 20.5 | 3.33
1440 | 0 | 0 | 0 | 19.5 | 0.56
1441 | 0 | 0 | 0 | 18.5 | 2.5
1442 | 0 | 0 | 0 | 17.7 | 2.22
1443 | 0 | 0 | 0 | 17.7 | 2.5
1444 | 0 | 0 | 0 | 17.6 | 1.67
1445 | 0 | 0 | 0 | 17.6 | 2.22
1446 | 61.1 | 13.9 | 242.9 | 17 | 3.06
1447 | 302.8 | 94.4 | 615.5 | 18.6 | 3.06
1448 | 475 | 188.9 | 513.9 | 20.4 | 4.44
1449 | 719.4 | 180.6 | 733.3 | 22.3 | 3.33
1450 | 847.2 | 161.1 | 797 | 25.7 | 3.33
1451 | 900 | 230.6 | 722.9 | 28.2 | 2.78
1452 | 780.6 | 213.9 | 611.9 | 29.2 | 3.61
1453 | 794.4 | 175 | 719.6 | 29.5 | 3.89
1454 | 672.2 | 205.6 | 635 | 30.3 | 4.44
1455 | 475 | 197.2 | 499 | 29.7 | 3.33
1456 | 227.8 | 111.1 | 344.7 | 29.2 | 2.78
1457 | 38.9 | 38.9 | 0 | 28.1 | 3.33
1458 | 0 | 0 | 0 | 26.4 | 3.33
1459 | 0 | 0 | 0 | 25.6 | 2.78
1460 | 0 | 0 | 0 | 23.9 | 2.78
1461 | 0 | 0 | 0 | 23 | 2.78
1462 | 0 | 0 | 0 | 22.7 | 3.33
1463 | 0 | 0 | 0 | 21.9 | 6.67
1464 | 0 | 0 | 0 | 20.4 | 0.83
1465 | 0 | 0 | 0 | 19.2 | 3.89
1466 | 0 | 0 | 0 | 17.8 | 2.5
1467 | 0 | 0 | 0 | 17.7 | 2.78
1468 | 0 | 0 | 0 | 17.7 | 2.78
1469 | 0 | 0 | 0 | 17.2 | 1.67
1470 | 88.9 | 27.8 | 249.3 | 16.3 | 2.22
1471 | 333.3 | 86.1 | 726.5 | 19 | 1.39
1472 | 561.1 | 102.8 | 820.4 | 22.5 | 2.22
1473 | 744.4 | 119.4 | 848 | 25.6 | 2.78
1474 | 869.4 | 119.4 | 868.9 | 27.5 | 3.89
1475 | 927.8 | 122.2 | 867.7 | 29 | 3.89
1476 | 916.7 | 133.3 | 843.7 | 29.8 | 4.44
1477 | 861.1 | 122.2 | 856.1 | 30.3 | 3.89
1478 | 730.6 | 116.7 | 832.9 | 31 | 3.89
1479 | 541.7 | 97.2 | 795.5 | 30.8 | 2.78
1480 | 311.1 | 77.8 | 685.7 | 30.5 | 4.44
1481 | 77.8 | 36.1 | 249.3 | 28.8 | 3.33
1482 | 0 | 0 | 0 | 25.5 | 3.33
1483 | 0 | 0 | 0 | 23.5 | 4.44
1484 | 0 | 0 | 0 | 22.5 | 3.33
1485 | 0 | 0 | 0 | 22.3 | 4.44
1486 | 0 | 0 | 0 | 21 | 4.44
1487 | 0 | 0 | 0 | 19.5 | 4.44
1488 | 0 | 0 | 0 | 17.8 | 1.11
1489 | 0 | 0 | 0 | 16.8 | 2.22
1490 | 0 | 0 | 0 | 15.6 | 2.22
1491 | 0 | 0 | 0 | 15.1 | 3.33
1492 | 0 | 0 | 0 | 14.9 | 3.33
1493 | 0 | 0 | 0 | 14.1 | 3.33
1494 | 91.7 | 8.3 | 255.6 | 14.2 | 2.22
1495 | 347.2 | 47.2 | 753 | 16.5 | 1.67
1496 | 580.6 | 72.2 | 892.4 | 21.7 | 2.78
1497 | 772.2 | 88.9 | 924.4 | 25.5 | 3.89
1498 | 897.2 | 102.8 | 918 | 27.6 | 6.11
1499 | 947.2 | 105.6 | 904.3 | 28.5 | 5
1500 | 944.4 | 105.6 | 901.3 | 29.5 | 5.56
1501 | 875 | 111.1 | 882.7 | 30 | 5.56
1502 | 738.9 | 111.1 | 849.3 | 30.7 | 5
1503 | 550 | 97.2 | 807.5 | 30.1 | 5
1504 | 319.4 | 77.8 | 706.4 | 29.5 | 6.11
1505 | 83.3 | 36.1 | 255.6 | 27.5 | 4.44
1506 | 0 | 0 | 0 | 24.5 | 3.89
1507 | 0 | 0 | 0 | 22.6 | 3.33
1508 | 0 | 0 | 0 | 21.6 | 3.33
1509 | 0 | 0 | 0 | 20.7 | 3.33
1510 | 0 | 0 | 0 | 19.5 | 2.78
1511 | 0 | 0 | 0 | 19 | 2.78
1512 | 0 | 0 | 0 | 18.4 | 1.39
1513 | 0 | 0 | 0 | 17.7 | 2.78
1514 | 0 | 0 | 0 | 17.5 | 2.78
1515 | 0 | 0 | 0 | 16.2 | 2.78
1516 | 0 | 0 | 0 | 16.7 | 3.33
1517 | 0 | 0 | 0 | 15.5 | 1.39
1518 | 80.6 | 27.8 | 261.9 | 15 | 2.22
1519 | 325 | 69.4 | 743.1 | 17.9 | 2.22
1520 | 561.1 | 97.2 | 824.4 | 22 | 2.78
1521 | 750 | 113.9 | 858.1 | 25 | 3.89
1522 | 875 | 119.4 | 870.8 | 27.6 | 5
1523 | 933.3 | 119.4 | 872.3 | 28.8 | 5.56
1524 | 919.4 | 119.4 | 857.4 | 29.4 | 5.56
1525 | 844.4 | 125 | 829.2 | 30 | 4.44
1526 | 719.4 | 122.2 | 805.6 | 30.5 | 5
1527 | 516.7 | 127.8 | 691.1 | 29.8 | 5
1528 | 291.7 | 88.9 | 589.6 | 29.5 | 3.33
1529 | 63.9 | 38.9 | 250.3 | 27.8 | 3.89
1530 | 0 | 0 | 0 | 24.5 | 2.78
1531 | 0 | 0 | 0 | 23.2 | 2.78
1532 | 0 | 0 | 0 | 22.5 | 3.33
1533 | 0 | 0 | 0 | 21.5 | 2.78
1534 | 0 | 0 | 0 | 21.3 | 4.44
1535 | 0 | 0 | 0 | 20.4 | 3.89
1536 | 0 | 0 | 0 | 19.4 | 1.67
1537 | 0 | 0 | 0 | 18 | 3.33
1538 | 0 | 0 | 0 | 17 | 2.78
1539 | 0 | 0 | 0 | 16.2 | 2.22
1540 | 0 | 0 | 0 | 16 | 2.78
1541 | 0 | 0 | 0 | 15.5 | 2.78
1542 | 80.6 | 27.8 | 268.1 | 15.6 | 3.89
1543 | 327.8 | 77.8 | 723.2 | 16.5 | 2.78
1544 | 572.2 | 97.2 | 841.2 | 21.6 | 2.78
1545 | 769.4 | 100 | 900.5 | 25.2 | 3.89
1546 | 891.7 | 111.1 | 897.4 | 27 | 6.11
1547 | 944.4 | 119.4 | 882.1 | 28.1 | 6.67
1548 | 930.6 | 119.4 | 867.3 | 29.4 | 5.56
1549 | 869.4 | 113.9 | 868.6 | 30 | 5
1550 | 750 | 105.6 | 866.9 | 29.9 | 5.56
1551 | 550 | 94.4 | 806.8 | 29.8 | 5.56
1552 | 319.4 | 75 | 707.1 | 29.1 | 5
1553 | 83.3 | 36.1 | 268.1 | 27.2 | 3.89
1554 | 0 | 0 | 0 | 24.5 | 3.89
1555 | 0 | 0 | 0 | 22.2 | 3.89
1556 | 0 | 0 | 0 | 21.8 | 2.22
1557 | 0 | 0 | 0 | 19.8 | 2.78
1558 | 0 | 0 | 0 | 19.1 | 2.78
1559 | 0 | 0 | 0 | 18.2 | 2.78
1560 | 0 | 0 | 0 | 17.3 | 1.94
1561 | 0 | 0 | 0 | 16.9 | 1.67
1562 | 0 | 0 | 0 | 16.9 | 1.67
1563 | 0 | 0 | 0 | 16.4 | 1.67
1564 | 0 | 0 | 0 | 14.6 | 1.67
1565 | 0 | 0 | 0 | 13.6 | 2.5
1566 | 66 | 27.8 | 254.3 | 14.9 | 1.67
1567 | 291.3 | 72.2 | 570.6 | 18.2 | 1.67
1568 | 517.8 | 100 | 652.7 | 22.7 | 1.94
1569 | 703.9 | 116.7 | 708.1 | 25.4 | 3.89
1570 | 880.6 | 119.4 | 872.8 | 27.4 | 4.44
1571 | 947.2 | 122.2 | 880 | 28.4 | 4.44
1572 | 938.9 | 119.4 | 874.1 | 29.6 | 2.78
1573 | 872.2 | 116.7 | 866.5 | 30.9 | 3.33
1574 | 741.7 | 100 | 860.7 | 30.9 | 4.17
1575 | 561.1 | 86.1 | 838.3 | 30.7 | 2.78
1576 | 327.8 | 61.1 | 758.1 | 30.5 | 3.33
1577 | 88.9 | 8.3 | 274.3 | 28.6 | 3.89
1578 | 0 | 0 | 0 | 25.4 | 2.78
1579 | 0 | 0 | 0 | 22.9 | 2.22
1580 | 0 | 0 | 0 | 21.9 | 3.89
1581 | 0 | 0 | 0 | 21 | 3.33
1582 | 0 | 0 | 0 | 20.4 | 2.78
1583 | 0 | 0 | 0 | 20.1 | 3.89
1584 | 0 | 0 | 0 | 18.7 | 2.22
1585 | 0 | 0 | 0 | 18.4 | 1.67
1586 | 0 | 0 | 0 | 16.7 | 2.22
1587 | 0 | 0 | 0 | 15.9 | 2.78
1588 | 0 | 0 | 0 | 15.9 | 2.22
1589 | 0 | 0 | 0 | 16.5 | 2.22
1590 | 88.9 | 30.6 | 280.5 | 15.8 | 2.22
1591 | 341.7 | 77.8 | 755.6 | 18.3 | 0.83
1592 | 572.2 | 102.8 | 825.7 | 22.5 | 1.94
1593 | 761.1 | 119.4 | 858.4 | 26.2 | 3.33
1594 | 877.8 | 119.4 | 867.5 | 28.5 | 4.44
1595 | 938.9 | 119.4 | 872 | 29.5 | 3.33
1596 | 941.7 | 119.4 | 875 | 31.3 | 3.33
1597 | 875 | 116.7 | 867.5 | 31.6 | 3.33
1598 | 741.7 | 100 | 858.4 | 32 | 3.33
1599 | 566.7 | 83.3 | 850.1 | 31.5 | 4.44
1600 | 333.3 | 61.1 | 759.8 | 31.1 | 3.89
1601 | 97.2 | 30.6 | 280.5 | 29.3 | 4.44
1602 | 0 | 0 | 0 | 25.7 | 4.44
1603 | 0 | 0 | 0 | 23.3 | 2.78
1604 | 0 | 0 | 0 | 21.8 | 2.5
1605 | 0 | 0 | 0 | 21.2 | 3.89
1606 | 0 | 0 | 0 | 20.4 | 3.33
1607 | 0 | 0 | 0 | 19.3 | 2.78
1608 | 0 | 0 | 0 | 18.4 | 2.5
1609 | 0 | 0 | 0 | 17.8 | 3.33
1610 | 0 | 0 | 0 | 17.3 | 2.78
1611 | 0 | 0 | 0 | 16.1 | 2.22
1612 | 0 | 0 | 0 | 15.5 | 2.22
1613 | 0 | 0 | 0 | 15 | 2.22
1614 | 86.1 | 25 | 286.6 | 14.9 | 1.11
1615 | 336.1 | 69.4 | 759.7 | 18.7 | 1.39
1616 | 552.8 | 105.6 | 784 | 22.3 | 1.94
1617 | 713.9 | 138.9 | 767.1 | 24.8 | 1.67
1618 | 847.2 | 144.4 | 802 | 28.1 | 2.22
1619 | 919.4 | 138.9 | 828.8 | 29.1 | 2.22
1620 | 922.2 | 130.6 | 840.6 | 31.3 | 2.78
1621 | 855.6 | 125 | 833.7 | 31.8 | 2.78
1622 | 730.6 | 116.7 | 819 | 32.4 | 2.78
1623 | 547.2 | 105.6 | 774.3 | 31.8 | 2.78
1624 | 313.9 | 63.9 | 712.2 | 32.3 | 4.44
1625 | 77.8 | 8.3 | 286.6 | 30.8 | 2.78
1626 | 0 | 0 | 0 | 27 | 4.44
1627 | 0 | 0 | 0 | 24.8 | 2.78
1628 | 0 | 0 | 0 | 23.5 | 2.78
1629 | 0 | 0 | 0 | 22.5 | 3.89
1630 | 0 | 0 | 0 | 20.9 | 3.89
1631 | 0 | 0 | 0 | 20.8 | 2.78
1632 | 0 | 0 | 0 | 19.7 | 2.78
1633 | 0 | 0 | 0 | 19 | 2.78
1634 | 0 | 0 | 0 | 18.3 | 2.78
1635 | 0 | 0 | 0 | 18.1 | 2.22
1636 | 0 | 0 | 0 | 18.1 | 2.78
1637 | 0 | 0 | 0 | 17.5 | 1.67
1638 | 77.8 | 27.5 | 254.3 | 17.8 | 2.78
1639 | 283.3 | 91.9 | 570.6 | 19.5 | 1.67
1640 | 525 | 183.3 | 597 | 23.4 | 2.78
1641 | 694.4 | 175 | 691.1 | 24.9 | 5.56
1642 | 827.8 | 172.2 | 746.4 | 26.7 | 6.11
1643 | 827.8 | 208.3 | 656.2 | 27.9 | 4.44
1644 | 858.3 | 219.4 | 676.8 | 28.8 | 3.89
1645 | 822.2 | 164.5 | 756.1 | 30.4 | 3.33
1646 | 658.3 | 164.1 | 703.8 | 30.5 | 2.78
1647 | 497.2 | 202.8 | 514.5 | 29.9 | 2.78
1648 | 191.7 | 125 | 189 | 30.7 | 1.67
1649 | 80.6 | 52.8 | 257.4 | 29.1 | 3.33
1650 | 0 | 0 | 0 | 27 | 3.33
1651 | 0 | 0 | 0 | 25.7 | 3.33
1652 | 0 | 0 | 0 | 24.4 | 2.22
1653 | 0 | 0 | 0 | 23.6 | 1.67
1654 | 0 | 0 | 0 | 23.8 | 2.22
1655 | 0 | 0 | 0 | 24.4 | 2.78
1656 | 0 | 0 | 0 | 23.9 | 3.06
1657 | 0 | 0 | 0 | 22.9 | 2.78
1658 | 0 | 0 | 0 | 22.2 | 3.33
1659 | 0 | 0 | 0 | 21.7 | 2.78
1660 | 0 | 0 | 0 | 20.9 | 2.78
1661 | 0 | 0 | 0 | 20.5 | 2.78
1662 | 22.2 | 25 | 0 | 20.5 | 3.33
1663 | 202.8 | 150 | 148.9 | 21.2 | 2.78
1664 | 302.8 | 219.4 | 145.1 | 23.5 | 3.89
1665 | 505.6 | 344.4 | 213.8 | 24.4 | 5
1666 | 597.2 | 313.9 | 321.8 | 26.4 | 4.44
1667 | 730.6 | 181.2 | 742.6 | 27.4 | 5
1668 | 808.3 | 173.5 | 769.9 | 28.9 | 5.56
1669 | 769.4 | 286.1 | 549 | 30.4 | 4.44
1670 | 733.3 | 213.9 | 689.3 | 30 | 4.44
1671 | 527.8 | 145.4 | 646.8 | 31 | 3.89
1672 | 197.2 | 99.3 | 526.8 | 30.7 | 3.89
1673 | 61.1 | 34.4 | 276.1 | 28.7 | 4.44
1674 | 0 | 0 | 0 | 27.9 | 5.56
1675 | 0 | 0 | 0 | 27.2 | 2.78
1676 | 0 | 0 | 0 | 26.6 | 2.22
1677 | 0 | 0 | 0 | 26.2 | 5
1678 | 0 | 0 | 0 | 25 | 4.44
1679 | 0 | 0 | 0 | 24.1 | 3.33
1680 | 0 | 0 | 0 | 23 | 3.33
1681 | 0 | 0 | 0 | 22 | 3.33
1682 | 0 | 0 | 0 | 20.9 | 2.78
1683 | 0 | 0 | 0 | 19.4 | 2.78
1684 | 0 | 0 | 0 | 18.4 | 2.78
1685 | 0 | 0 | 0 | 18.2 | 2.78
1686 | 86.1 | 30.6 | 304.7 | 17.9 | 1.39
1687 | 341.7 | 63.9 | 766.2 | 20.3 | 1.67
1688 | 577.8 | 77.8 | 868 | 24.4 | 2.78
1689 | 761.1 | 80.6 | 900.8 | 25.5 | 3.89
1690 | 880.6 | 91.7 | 894 | 27.4 | 4.44
1691 | 936.1 | 97.2 | 884.8 | 28.7 | 4.44
1692 | 933.3 | 94.4 | 884.8 | 29.9 | 3.89
1693 | 836.1 | 94.4 | 840.5 | 30.9 | 5.56
1694 | 708.3 | 141.7 | 750 | 30.8 | 4.44
1695 | 547.2 | 150 | 689.5 | 31.2 | 5
1696 | 238.9 | 75 | 460 | 30.5 | 5.56
1697 | 33.3 | 11.1 | 199.9 | 29.4 | 7.22
1698 | 0 | 0 | 0 | 27.6 | 2.78
1699 | 0 | 0 | 0 | 26.4 | 1.39
1700 | 0 | 0 | 0 | 24.8 | 2.22
1701 | 0 | 0 | 0 | 23.7 | 1.67
1702 | 0 | 0 | 0 | 23.2 | 1.67
1703 | 0 | 0 | 0 | 22.7 | 0.56
1704 | 0 | 0 | 0 | 20.9 | 3.61
1705 | 0 | 0 | 0 | 21.1 | 2.78
1706 | 0 | 0 | 0 | 20.7 | 1.67
1707 | 0 | 0 | 0 | 20.5 | 2.78
1708 | 0 | 0 | 0 | 20.4 | 2.78
1709 | 0 | 0 | 0 | 19.2 | 2.78
1710 | 52.8 | 19.4 | 295.6 | 18.9 | 2.78
1711 | 283.3 | 116.7 | 465.5 | 21 | 3.33
1712 | 513.9 | 186.1 | 567.2 | 24 | 4.44
1713 | 658.3 | 205.6 | 597.8 | 25.9 | 5.56
1714 | 827.8 | 213.9 | 694.2 | 27.8 | 5
1715 | 730.6 | 291.7 | 461.9 | 29.9 | 5.56
1716 | 900 | 225 | 710.5 | 30.5 | 4.44
1717 | 818.3 | 164.5 | 756.1 | 31.3 | 4.44
1718 | 698.6 | 164.1 | 703.8 | 32.4 | 5.56
1719 | 513.9 | 166.7 | 600.8 | 32.4 | 5.56
1720 | 333.3 | 86.1 | 690.5 | 31 | 4.44
1721 | 86.1 | 41.7 | 310.6 | 30 | 2.78
1722 | 0 | 0 | 0 | 28.2 | 1.67
1723 | 0 | 0 | 0 | 25.8 | 1.67
1724 | 0 | 0 | 0 | 24 | 3.33
1725 | 0 | 0 | 0 | 22.6 | 3.33
1726 | 0 | 0 | 0 | 21.9 | 2.78
1727 | 0 | 0 | 0 | 21.5 | 1.67
1728 | 0 | 0 | 0 | 20.9 | 3.89
1729 | 0 | 0 | 0 | 20.4 | 1.39
1730 | 0 | 0 | 0 | 20 | 1.11
1731 | 0 | 0 | 0 | 19.6 | 2.22
1732 | 0 | 0 | 0 | 19.7 | 2.22
1733 | 0 | 0 | 0 | 19.4 | 1.67
1734 | 55.6 | 30.6 | 218.5 | 19.5 | 1.67
1735 | 258.3 | 122.2 | 378.4 | 21.1 | 2.78
1736 | 422.2 | 213.9 | 359.4 | 23.1 | 3.89
1737 | 703.9 | 162.6 | 708.1 | 24.6 | 4.44
1738 | 838.4 | 180.5 | 746.6 | 27 | 3.89
1739 | 813.9 | 291.7 | 548.5 | 28 | 4.44
1740 | 908.3 | 283.3 | 656.5 | 30.1 | 3.33
1741 | 511.1 | 263.9 | 278.9 | 31.4 | 2.78
1742 | 416.7 | 247.2 | 223.2 | 33 | 2.78
1743 | 416.7 | 177.8 | 412.1 | 31.3 | 3.33
1744 | 133.3 | 127.8 | 15.4 | 30.9 | 3.89
1745 | 83.3 | 44.4 | 316.4 | 29.3 | 3.89
1746 | 0 | 0 | 0 | 27.1 | 2.78
1747 | 0 | 0 | 0 | 25.7 | 2.22
1748 | 0 | 0 | 0 | 25 | 1.67
1749 | 0 | 0 | 0 | 24.3 | 3.89
1750 | 0 | 0 | 0 | 23.4 | 3.89
1751 | 0 | 0 | 0 | 22.4 | 5
1752 | 0 | 0 | 0 | 22.3 | 4.17
1753 | 0 | 0 | 0 | 22.1 | 4.44
1754 | 0 | 0 | 0 | 21.4 | 3.33
1755 | 0 | 0 | 0 | 21 | 2.78
1756 | 0 | 0 | 0 | 20.9 | 2.78
1757 | 0 | 0 | 0 | 20.9 | 2.78
1758 | 38.9 | 30.6 | 71.8 | 20.8 | 2.78
1759 | 227.8 | 138.9 | 245.9 | 21.6 | 2.22
1760 | 516.7 | 136.5 | 652.7 | 23.9 | 3.89
1761 | 702.8 | 162.6 | 708.1 | 27 | 3.89
1762 | 691.7 | 313.9 | 425.3 | 28.5 | 4.44
1763 | 930.6 | 181.2 | 742.6 | 29 | 3.89
1764 | 602.8 | 173.5 | 769.9 | 30.6 | 3.33
1765 | 652.8 | 164.5 | 756.1 | 31.9 | 3.89
1766 | 600 | 211.1 | 510.9 | 31 | 4.44
1767 | 297.2 | 158.3 | 238.9 | 31.2 | 3.33
1768 | 225 | 91.7 | 368.9 | 30.9 | 2.78
1769 | 69.4 | 16.7 | 322.2 | 28.9 | 2.78
1770 | 0 | 0 | 0 | 27.4 | 3.89
1771 | 0 | 0 | 0 | 21.3 | 5
1772 | 0 | 0 | 0 | 21.7 | 4.44
1773 | 0 | 0 | 0 | 22 | 2.78
1774 | 0 | 0 | 0 | 22.6 | 2.22
1775 | 0 | 0 | 0 | 23 | 3.89
1776 | 0 | 0 | 0 | 23 | 4.44
1777 | 0 | 0 | 0 | 22.7 | 3.89
1778 | 0 | 0 | 0 | 19.6 | 1.11
1779 | 0 | 0 | 0 | 18.2 | 5
1780 | 0 | 0 | 0 | 18.7 | 1.11
1781 | 0 | 0 | 0 | 18.8 | 2.78
1782 | 27.8 | 41.7 | 0 | 19.2 | 0.56
1783 | 186.1 | 91.9 | 570.6 | 19.2 | 2.22
1784 | 525 | 208.3 | 542.9 | 21.8 | 2.22
1785 | 483.3 | 369.4 | 149.3 | 22.6 | 2.78
1786 | 736.1 | 516.7 | 246.6 | 23.3 | 3.33
1787 | 544.4 | 466.7 | 81.4 | 25.9 | 1.67
1788 | 988.9 | 316.7 | 703.3 | 27.3 | 5
1789 | 858.3 | 164.5 | 756.1 | 28.4 | 2.22
1790 | 686.1 | 169.4 | 677.2 | 29.5 | 1.67
1791 | 444.4 | 163.9 | 481 | 29.6 | 0.56
1792 | 255.6 | 122.2 | 367.2 | 29.5 | 1.67
1793 | 55.6 | 34.4 | 276.1 | 28.3 | 1.67
1794 | 0 | 0 | 0 | 26.8 | 0.56
1795 | 0 | 0 | 0 | 25.9 | 0
1796 | 0 | 0 | 0 | 24.9 | 0
1797 | 0 | 0 | 0 | 24.8 | 0
1798 | 0 | 0 | 0 | 24.8 | 0
1799 | 0 | 0 | 0 | 23.8 | 0
1800 | 0 | 0 | 0 | 23.9 | 4.72
1801 | 0 | 0 | 0 | 23.6 | 3.33
1802 | 0 | 0 | 0 | 23.2 | 2.78
1803 | 0 | 0 | 0 | 23.2 | 1.67
1804 | 0 | 0 | 0 | 22.2 | 0.56
1805 | 0 | 0 | 0 | 21.9 | 2.22
1806 | 63.9 | 22.2 | 333.6 | 21.8 | 0.56
1807 | 283.3 | 94.4 | 517.8 | 22.7 | 0.56
1808 | 500 | 150 | 598.3 | 24.5 | 2.78
1809 | 675 | 183.3 | 642.9 | 25.5 | 1.67
1810 | 819.4 | 288.9 | 594.9 | 27.3 | 3.33
1811 | 825 | 181.2 | 742.6 | 28.5 | 3.89
1812 | 911.1 | 173.5 | 769.9 | 29.2 | 3.89
1813 | 863.9 | 164.5 | 756.1 | 29.7 | 2.78
1814 | 708.3 | 258.3 | 588.4 | 30.3 | 2.22
1815 | 516.7 | 197.2 | 546.1 | 30.8 | 2.22
1816 | 311.1 | 102.8 | 571.1 | 30.4 | 3.89
1817 | 80.6 | 38.9 | 333.6 | 29.8 | 1.67
1818 | 0 | 0 | 0 | 26.3 | 1.67
1819 | 0 | 0 | 0 | 24.4 | 3.33
1820 | 0 | 0 | 0 | 24.1 | 2.78
1821 | 0 | 0 | 0 | 23.8 | 2.78
1822 | 0 | 0 | 0 | 23.9 | 0
1823 | 0 | 0 | 0 | 23.5 | 5
1824 | 0 | 0 | 0 | 23 | 5
1825 | 0 | 0 | 0 | 22.6 | 2.22
1826 | 0 | 0 | 0 | 22 | 2.22
1827 | 0 | 0 | 0 | 21.6 | 2.22
1828 | 0 | 0 | 0 | 21.3 | 1.67
1829 | 0 | 0 | 0 | 21 | 2.78
1830 | 41.7 | 25 | 137.9 | 20.8 | 2.22
1831 | 272.2 | 77.8 | 530.6 | 22.1 | 2.78
1832 | 502.8 | 111.1 | 667.6 | 25.4 | 3.89
1833 | 741.7 | 125 | 804.5 | 27.6 | 4.44
1834 | 894.4 | 141.7 | 842.4 | 28.6 | 7.22
1835 | 972.2 | 138.9 | 868.5 | 29.7 | 5
1836 | 966.7 | 147.2 | 854.1 | 31 | 3.89
1837 | 905.6 | 138.9 | 857.9 | 30.7 | 3.89
1838 | 763.9 | 144.4 | 808.1 | 31.3 | 2.78
1839 | 547.2 | 113.9 | 738.6 | 30.7 | 2.78
1840 | 319.4 | 66.7 | 689.8 | 30.9 | 1.67
1841 | 86.1 | 19.4 | 339.2 | 30.6 | 1.11
1842 | 0 | 0 | 0 | 29.5 | 1.67
1843 | 0 | 0 | 0 | 28.7 | 1.11
1844 | 0 | 0 | 0 | 26 | 0
1845 | 0 | 0 | 0 | 25.1 | 0
1846 | 0 | 0 | 0 | 23.8 | 0
1847 | 0 | 0 | 0 | 24.7 | 2.22
1848 | 0 | 0 | 0 | 24.1 | 5.28
1849 | 0 | 0 | 0 | 22.8 | 1.67
1850 | 0 | 0 | 0 | 22.1 | 3.33
1851 | 0 | 0 | 0 | 21.7 | 2.78
1852 | 0 | 0 | 0 | 21.2 | 2.22
1853 | 0 | 0 | 0 | 21 | 2.22
1854 | 58.3 | 22.2 | 295 | 20.9 | 1.94
1855 | 283.3 | 97.2 | 505.6 | 23.2 | 1.94
1856 | 525 | 122.2 | 684.6 | 25.2 | 2.78
1857 | 716.7 | 136.1 | 755.7 | 28.3 | 3.33
1858 | 847.2 | 141.7 | 788 | 29.4 | 3.33
1859 | 913.9 | 138.9 | 806.3 | 30.3 | 2.22
1860 | 830.6 | 183.3 | 673.3 | 30.9 | 1.11
1861 | 863.9 | 186.1 | 757 | 31.9 | 2.78
1862 | 730.6 | 161.1 | 741.3 | 32.8 | 2.78
1863 | 533.3 | 147.2 | 656.2 | 32.4 | 2.78
1864 | 294.4 | 88.9 | 558.4 | 32.4 | 2.78
1865 | 55.6 | 22.2 | 272.3 | 31.9 | 1.11
1866 | 0 | 0 | 0 | 30 | 0
1867 | 0 | 0 | 0 | 28 | 0
1868 | 0 | 0 | 0 | 27.3 | 2.78
1869 | 0 | 0 | 0 | 26.8 | 2.22
1870 | 0 | 0 | 0 | 26.1 | 0.56
1871 | 0 | 0 | 0 | 25.8 | 2.22
1872 | 0 | 0 | 0 | 25.8 | 5.56
1873 | 0 | 0 | 0 | 24.2 | 3.89
1874 | 0 | 0 | 0 | 23.2 | 3.33
1875 | 0 | 0 | 0 | 22.9 | 2.78
1876 | 0 | 0 | 0 | 22.3 | 1.11
1877 | 0 | 0 | 0 | 21.9 | 1.67
1878 | 61.1 | 27.8 | 268.8 | 21.6 | 2.22
1879 | 291.7 | 94.4 | 533.4 | 22.9 | 2.22
1880 | 527.8 | 136.1 | 663.8 | 26 | 3.89
1881 | 716.7 | 158.3 | 725.2 | 27.8 | 3.89
1882 | 847.2 | 175 | 749.4 | 29.3 | 3.89
1883 | 900 | 238.9 | 686.6 | 29.8 | 4.44
1884 | 947.2 | 252.8 | 721.2 | 31.5 | 3.33
1885 | 886.1 | 266.7 | 690.5 | 31.7 | 4.44
1886 | 647.2 | 164.1 | 703.8 | 32.2 | 2.78
1887 | 583.3 | 145.4 | 646.8 | 31.9 | 2.78
1888 | 277.8 | 99.3 | 526.8 | 28.8 | 3.89
1889 | 38.9 | 34.4 | 276.1 | 22.8 | 5.56
1890 | 0 | 0 | 0 | 23.2 | 3.89
1891 | 0 | 0 | 0 | 22.8 | 2.78
1892 | 0 | 0 | 0 | 22.9 | 2.78
1893 | 0 | 0 | 0 | 21.8 | 2.22
1894 | 0 | 0 | 0 | 21.2 | 5
1895 | 0 | 0 | 0 | 20.8 | 5
1896 | 0 | 0 | 0 | 20.8 | 5.83
1897 | 0 | 0 | 0 | 20.8 | 1.67
1898 | 0 | 0 | 0 | 20.8 | 0.56
1899 | 0 | 0 | 0 | 20.9 | 0.56
1900 | 0 | 0 | 0 | 21.1 | 0.56
1901 | 0 | 0 | 0 | 21.3 | 2.22
1902 | 47.2 | 11.1 | 287.5 | 21.3 | 2.22
1903 | 308.3 | 88.9 | 591 | 22.2 | 2.22
1904 | 516.7 | 138.9 | 638.5 | 24.4 | 2.78
1905 | 702.8 | 147.2 | 720.1 | 26.1 | 2.78
1906 | 833.3 | 150 | 760.3 | 27.5 | 2.78
1907 | 880.6 | 161.1 | 745.9 | 29.9 | 1.11
1908 | 877.8 | 155.6 | 748.8 | 30.4 | 1.67
1909 | 847.2 | 186.1 | 735.6 | 31.1 | 2.78
1910 | 697.2 | 180.6 | 669.7 | 31.8 | 2.22
1911 | 513.9 | 172.2 | 577.5 | 32.4 | 2.5
1912 | 266.7 | 150 | 314.2 | 32.4 | 2.22
1913 | 88.9 | 36.1 | 355.5 | 25.6 | 4.44
1914 | 0 | 0 | 0 | 25.1 | 3.89
1915 | 0 | 0 | 0 | 24.1 | 2.22
1916 | 0 | 0 | 0 | 23.7 | 2.22
1917 | 0 | 0 | 0 | 22.9 | 1.67
1918 | 0 | 0 | 0 | 22.2 | 2.22
1919 | 0 | 0 | 0 | 21.9 | 2.22
1920 | 0 | 0 | 0 | 21.5 | 6.11
1921 | 0 | 0 | 0 | 21.6 | 2.22
1922 | 0 | 0 | 0 | 21.4 | 0.56
1923 | 0 | 0 | 0 | 21.4 | 0.56
1924 | 0 | 0 | 0 | 20.9 | 1.67
1925 | 0 | 0 | 0 | 20.3 | 1.67
1926 | 63.9 | 27.8 | 283.9 | 20.6 | 1.67
1927 | 286.1 | 86.1 | 536.3 | 22.3 | 1.39
1928 | 497.2 | 152.8 | 580.6 | 24.2 | 1.67
1929 | 683.3 | 200 | 625.2 | 25.8 | 1.67
1930 | 838.9 | 175 | 737.4 | 27.5 | 2.78
1931 | 880.6 | 180.6 | 724.5 | 30.4 | 2.78
1932 | 850 | 213.9 | 658.4 | 31.4 | 1.67
1933 | 819.4 | 269.4 | 610.9 | 31.6 | 2.78
1934 | 719.4 | 236.1 | 625.2 | 31.1 | 4.44
1935 | 538.9 | 152.8 | 650.9 | 31.6 | 4.44
1936 | 233.3 | 122.2 | 297.9 | 31.1 | 4.44
1937 | 47.2 | 61.1 | 0 | 29.5 | 5
1938 | 0 | 0 | 0 | 26.5 | 2.78
1939 | 0 | 0 | 0 | 25.5 | 2.78
1940 | 0 | 0 | 0 | 24.9 | 2.78
1941 | 0 | 0 | 0 | 24 | 4.44
1942 | 0 | 0 | 0 | 22.7 | 3.89
1943 | 0 | 0 | 0 | 21.7 | 2.78
1944 | 0 | 0 | 0 | 21.2 | 6.39
1945 | 0 | 0 | 0 | 20.7 | 0.56
1946 | 0 | 0 | 0 | 20.6 | 1.67
1947 | 0 | 0 | 0 | 20.2 | 1.67
1948 | 0 | 0 | 0 | 19.3 | 2.22
1949 | 0 | 0 | 0 | 18.5 | 1.67
1950 | 77.8 | 30.6 | 366 | 18.8 | 1.11
1951 | 322.2 | 80.6 | 645.3 | 22 | 0.56
1952 | 550 | 108.3 | 742.5 | 25.3 | 1.67
1953 | 747.2 | 130.6 | 796 | 29.1 | 2.78
1954 | 875 | 136.1 | 819.3 | 30.5 | 5
1955 | 916.7 | 133.3 | 809.5 | 31.2 | 5
1956 | 911.1 | 141.7 | 795.1 | 32.1 | 5.56
1957 | 852.8 | 138.9 | 791.6 | 32.1 | 5
1958 | 719.4 | 130.6 | 760.2 | 31.47 | 5.56
1959 | 525 | 119.4 | 681.8 | 31.31 | 4.44
1960 | 294.4 | 88.9 | 548.9 | 30.82 | 5.56
1961 | 66.7 | 47.2 | 151 | 29.4 | 4.44
1962 | 0 | 0 | 0 | 26.4 | 4.44
1963 | 0 | 0 | 0 | 24.6 | 3.89
1964 | 0 | 0 | 0 | 23.5 | 2.78
1965 | 0 | 0 | 0 | 23.3 | 2.78
1966 | 0 | 0 | 0 | 21.6 | 3.89
1967 | 0 | 0 | 0 | 20.8 | 2.22
1968 | 0 | 0 | 0 | 20.1 | 6.67
1969 | 0 | 0 | 0 | 19.6 | 0.56
1970 | 0 | 0 | 0 | 19.1 | 0
1971 | 0 | 0 | 0 | 18.6 | 0.56
1972 | 0 | 0 | 0 | 17.6 | 1.11
1973 | 0 | 0 | 0 | 17.5 | 0.56
1974 | 91.7 | 36.1 | 371.1 | 17.1 | 0
1975 | 330.6 | 102.8 | 605.7 | 19.7 | 0
1976 | 544.4 | 138.9 | 680.1 | 24.6 | 1.67
1977 | 761.1 | 158.3 | 776.6 | 28 | 3.33
1978 | 886.1 | 161.1 | 802.5 | 29 | 4.44
1979 | 947.2 | 163.9 | 808.2 | 30.1 | 5.56
1980 | 927.8 | 175 | 776.7 | 30.6 | 5.56
1981 | 872.2 | 175 | 771.8 | 31.4 | 5.56
1982 | 744.4 | 163.9 | 747.9 | 31.1 | 7.22
1983 | 563.9 | 138.9 | 712.7 | 30.6 | 7.22
1984 | 347.2 | 113.9 | 620.5 | 29.7 | 7.22
1985 | 105.6 | 69.4 | 277 | 28.1 | 5.56
1986 | 0 | 0 | 0 | 25.9 | 5.56
1987 | 0 | 0 | 0 | 25.1 | 4.44
1988 | 0 | 0 | 0 | 23.1 | 3.89
1989 | 0 | 0 | 0 | 22.1 | 3.33
1990 | 0 | 0 | 0 | 20.1 | 2.78
1991 | 0 | 0 | 0 | 19.7 | 2.22
1992 | 0 | 0 | 0 | 20.84 | 6.94
1993 | 0 | 0 | 0 | 20.21 | 1.11
1994 | 0 | 0 | 0 | 19.53 | 0.56
1995 | 0 | 0 | 0 | 18.96 | 0
1996 | 0 | 0 | 0 | 18.53 | 0
1997 | 0 | 0 | 0 | 18.18 | 0
1998 | 94.4 | 27.5 | 254.3 | 18.11 | 0
1999 | 352.8 | 102.8 | 662.1 | 20.14 | 0.56
2000 | 594.4 | 136.5 | 652.7 | 23.61 | 0.56
2001 | 769.4 | 161.1 | 782.2 | 25.93 | 2.78
2002 | 905.6 | 163.9 | 819.6 | 27.88 | 4.44
2003 | 975 | 181.2 | 742.6 | 29.29 | 5.56
2004 | 958.3 | 166.7 | 815.6 | 30.49 | 5.56
2005 | 900 | 163.9 | 813.5 | 31.15 | 5.56
2006 | 766.7 | 164.1 | 703.8 | 31.47 | 5.56
2007 | 580.6 | 158.3 | 706.2 | 31.31 | 5.56
2008 | 366.7 | 102.8 | 698.9 | 30.82 | 5.56
2009 | 119.4 | 22.2 | 376.2 | 28.91 | 5
2010 | 0 | 0 | 0 | 26.56 | 2.78
2011 | 0 | 0 | 0 | 24.94 | 1.67
2012 | 0 | 0 | 0 | 23.62 | 2.22
2013 | 0 | 0 | 0 | 22.98 | 2.22
2014 | 0 | 0 | 0 | 22.23 | 1.67
2015 | 0 | 0 | 0 | 21.71 | 1.67
2016 | 0 | 0 | 0 | 18.2 | 7.22
2017 | 0 | 0 | 0 | 18.2 | 1.67
2018 | 0 | 0 | 0 | 17.8 | 1.67
2019 | 0 | 0 | 0 | 17.3 | 1.67
2020 | 0 | 0 | 0 | 16.7 | 1.11
2021 | 0 | 0 | 0 | 15.8 | 1.11
2022 | 72.2 | 44.4 | 208.1 | 15.3 | 0
2023 | 302.8 | 91.9 | 570.6 | 19.3 | 0
2024 | 580.6 | 136.5 | 652.7 | 25.1 | 1.11
2025 | 761.1 | 138.9 | 798.6 | 27.7 | 2.78
2026 | 900 | 141.7 | 836.8 | 29.8 | 4.44
2027 | 969.4 | 138.9 | 854.4 | 30.8 | 3.89
2028 | 961.1 | 147.2 | 837.2 | 31.8 | 5
2029 | 897.2 | 147.2 | 827.6 | 31.9 | 5.56
2030 | 763.9 | 127.8 | 816.4 | 32.3 | 5.56
2031 | 580.6 | 113.9 | 778.7 | 32.5 | 5
2032 | 344.4 | 88.9 | 674.1 | 31.8 | 5
2033 | 100 | 41.7 | 381.2 | 30.3 | 3.89
2034 | 0 | 0 | 0 | 24.7 | 4.44
2035 | 0 | 0 | 0 | 26.1 | 2.78
2036 | 0 | 0 | 0 | 22.8 | 2.78
2037 | 0 | 0 | 0 | 21.8 | 2.22
2038 | 0 | 0 | 0 | 21.1 | 2.78
2039 | 0 | 0 | 0 | 20.7 | 2.22
2040 | 0 | 0 | 0 | 20.9 | 7.5
2041 | 0 | 0 | 0 | 19.7 | 2.22
2042 | 0 | 0 | 0 | 18.2 | 2.22
2043 | 0 | 0 | 0 | 17.5 | 2.22
2044 | 0 | 0 | 0 | 17.5 | 2.22
2045 | 0 | 0 | 0 | 16.7 | 2.22
2046 | 66.7 | 27.5 | 254.3 | 17.3 | 1.67
2047 | 297.2 | 91.9 | 570.6 | 19.6 | 0.56
2048 | 536.1 | 136.1 | 665.8 | 24.3 | 1.11
2049 | 730.6 | 161.1 | 729.6 | 26.7 | 1.67
2050 | 866.7 | 183.3 | 752.9 | 29.2 | 2.78
2051 | 922.2 | 188.9 | 753.3 | 31.8 | 4.44
2052 | 913.9 | 194.4 | 739.1 | 32.7 | 5
2053 | 855.6 | 175 | 749.8 | 33.5 | 5.56
2054 | 711.1 | 163.9 | 701.1 | 33.8 | 5
2055 | 533.3 | 141.7 | 651.9 | 33.6 | 5
2056 | 302.8 | 99.3 | 526.8 | 32.8 | 3.89
2057 | 77.8 | 22.2 | 386.1 | 30.8 | 5
2058 | 0 | 0 | 0 | 27.3 | 3.89
2059 | 0 | 0 | 0 | 24.9 | 2.78
2060 | 0 | 0 | 0 | 23.4 | 2.78
2061 | 0 | 0 | 0 | 22.6 | 2.78
2062 | 0 | 0 | 0 | 21.5 | 2.78
2063 | 0 | 0 | 0 | 20.8 | 2.78
2064 | 0 | 0 | 0 | 20 | 7.78
2065 | 0 | 0 | 0 | 19.9 | 2.22
2066 | 0 | 0 | 0 | 20.1 | 2.22
2067 | 0 | 0 | 0 | 19.1 | 2.22
2068 | 0 | 0 | 0 | 17.6 | 0
2069 | 0 | 0 | 0 | 18.6 | 0
2070 | 58.3 | 33.3 | 183.1 | 17.6 | 0
2071 | 275 | 91.9 | 570.6 | 19.7 | 0
2072 | 472.2 | 136.5 | 652.7 | 25 | 0
2073 | 658.3 | 188.9 | 600.4 | 27.3 | 1.67
2074 | 844.4 | 205.6 | 702.9 | 30.8 | 1.67
2075 | 908.3 | 202.8 | 723.8 | 32.1 | 3.89
2076 | 916.7 | 205.6 | 729.5 | 33.5 | 3.89
2077 | 847.2 | 164.5 | 756.1 | 34.3 | 5
2078 | 711.1 | 164.1 | 703.8 | 34.3 | 5
2079 | 533.3 | 145.4 | 646.8 | 34 | 5
2080 | 302.8 | 99.3 | 526.8 | 33.6 | 5.56
2081 | 75 | 34.4 | 276.1 | 30.8 | 5
2082 | 0 | 0 | 0 | 27.4 | 5
2083 | 0 | 0 | 0 | 25.8 | 3.89
2084 | 0 | 0 | 0 | 24.1 | 3.33
2085 | 0 | 0 | 0 | 22.5 | 3.33
2086 | 0 | 0 | 0 | 21.8 | 3.33
2087 | 0 | 0 | 0 | 20.7 | 2.22
2088 | 0 | 0 | 0 | 20.4 | 8.06
2089 | 0 | 0 | 0 | 19.3 | 2.22
2090 | 0 | 0 | 0 | 19.5 | 2.22
2091 | 0 | 0 | 0 | 18.4 | 2.22
2092 | 0 | 0 | 0 | 17.3 | 1.67
2093 | 0 | 0 | 0 | 17.2 | 0
2094 | 61.1 | 41.7 | 140.8 | 17.7 | 1.11
2095 | 286.1 | 91.9 | 570.6 | 20.6 | 0.56
2096 | 516.7 | 136.5 | 652.7 | 24.5 | 1.67
2097 | 711.1 | 200 | 652.6 | 26.7 | 1.67
2098 | 847.2 | 205.6 | 704.9 | 29.2 | 1.67
2099 | 902.8 | 216.7 | 703 | 31.4 | 2.22
2100 | 908.3 | 211.1 | 714.3 | 33.1 | 2.78
2101 | 841.7 | 164.5 | 756.1 | 33.5 | 5.56
2102 | 713.9 | 164.1 | 703.8 | 33.6 | 5.56
2103 | 527.8 | 145.4 | 646.8 | 33.6 | 5.56
2104 | 302.8 | 99.3 | 526.8 | 32.5 | 5.56
2105 | 80.6 | 34.4 | 276.1 | 30.2 | 5.56
2106 | 0 | 0 | 0 | 27 | 5
2107 | 0 | 0 | 0 | 24.9 | 3.89
2108 | 0 | 0 | 0 | 23.5 | 4.44
2109 | 0 | 0 | 0 | 22.6 | 2.78
2110 | 0 | 0 | 0 | 21.7 | 2.78
2111 | 0 | 0 | 0 | 21.2 | 2.22
2112 | 0 | 0 | 0 | 20.84 | 8.33
2113 | 0 | 0 | 0 | 20.21 | 1.67
2114 | 0 | 0 | 0 | 19.53 | 2.78
2115 | 0 | 0 | 0 | 18.96 | 2.78
2116 | 0 | 0 | 0 | 18.53 | 2.22
2117 | 0 | 0 | 0 | 18.18 | 2.22
2118 | 66 | 27.5 | 254.3 | 18.11 | 1.67
2119 | 291.3 | 91.9 | 570.6 | 20.14 | 1.67
2120 | 533.3 | 136.5 | 652.7 | 23.61 | 2.22
2121 | 733.3 | 162.6 | 708.1 | 25.93 | 2.22
2122 | 858.3 | 155.6 | 771 | 27.88 | 2.78
2123 | 911.1 | 152.8 | 776 | 29.29 | 5
2124 | 902.8 | 147.2 | 773.2 | 30.49 | 5.56
2125 | 825 | 150 | 740.5 | 31.15 | 5.56
2126 | 680.6 | 155.6 | 669.2 | 31.47 | 7.78
2127 | 523.2 | 145.4 | 646.8 | 31.31 | 7.22
2128 | 286.8 | 99.3 | 526.8 | 30.82 | 6.67
2129 | 76.3 | 34.4 | 276.1 | 28.91 | 5.56
2130 | 0 | 0 | 0 | 28.5 | 5.56
2131 | 0 | 0 | 0 | 27.1 | 4.44
2132 | 0 | 0 | 0 | 20.9 | 2.78
2133 | 0 | 0 | 0 | 24.2 | 2.22
2134 | 0 | 0 | 0 | 23.8 | 1.11
2135 | 0 | 0 | 0 | 22.6 | 1.67
2136 | 0 | 0 | 0 | 20.84 | 8.61
2137 | 0 | 0 | 0 | 20.21 | 1.67
2138 | 0 | 0 | 0 | 19.53 | 1.67
2139 | 0 | 0 | 0 | 18.96 | 1.11
2140 | 0 | 0 | 0 | 18.53 | 1.67
2141 | 0 | 0 | 0 | 18.18 | 2.22
2142 | 63.9 | 27.8 | 255.9 | 18.11 | 2.22
2143 | 236.1 | 102.8 | 345.1 | 20.14 | 1.11
2144 | 433.3 | 125 | 508.6 | 23.61 | 1.67
2145 | 600 | 138.9 | 586.8 | 25.93 | 2.78
2146 | 711.1 | 180.5 | 746.6 | 27.88 | 4.44
2147 | 769.4 | 141.7 | 641.6 | 29.29 | 4.44
2148 | 775 | 141.7 | 647.3 | 30.49 | 5.56
2149 | 730.6 | 136.1 | 651.3 | 31.15 | 5.56
2150 | 644.4 | 125 | 661.1 | 31.47 | 5.56
2151 | 502.8 | 138.9 | 600.3 | 31.31 | 5.56
2152 | 325 | 155.6 | 438.6 | 30.82 | 5.56
2153 | 122.2 | 34.4 | 276.1 | 28.91 | 5.56
2154 | 0 | 0 | 0 | 28 | 4.44
2155 | 0 | 0 | 0 | 26.2 | 2.78
2156 | 0 | 0 | 0 | 25.1 | 2.78
2157 | 0 | 0 | 0 | 24.8 | 2.78
2158 | 0 | 0 | 0 | 24.7 | 2.78
2159 | 0 | 0 | 0 | 24.9 | 1.67
2160 | 0 | 0 | 0 | 25.3 | 0.28
2161 | 0 | 0 | 0 | 24.1 | 1.39
2162 | 0 | 0 | 0 | 23.5 | 1.94
2163 | 0 | 0 | 0 | 22.9 | 1.39
2164 | 0 | 0 | 0 | 22.4 | 1.67
2165 | 5.6 | 2.8 | 0 | 21.9 | 1.67
2166 | 97.2 | 61.1 | 253.2 | 22.2 | 0.83
2167 | 258.3 | 158.3 | 257.9 | 24 | 0.56
2168 | 569.4 | 172.2 | 653.9 | 25 | 1.11
2169 | 758.3 | 172.2 | 744.8 | 26.8 | 1.67
2170 | 869.4 | 180.6 | 753.8 | 28.7 | 1.67
2171 | 808.3 | 161.1 | 660.8 | 31.2 | 1.67
2172 | 800 | 188.9 | 623.9 | 31.7 | 3.33
2173 | 544.4 | 219.4 | 355.6 | 32.6 | 2.78
2174 | 722.2 | 252.8 | 596.5 | 32.1 | 2.78
2175 | 213.9 | 152.8 | 100.6 | 33.9 | 1.11
2176 | 230.6 | 127.8 | 265.1 | 33.8 | 2.78
2177 | 36.1 | 19.4 | 116.9 | 32.8 | 2.22
2178 | 0 | 0 | 0 | 31.4 | 1.67
2179 | 0 | 0 | 0 | 30 | 3.89
2180 | 0 | 0 | 0 | 27.9 | 4.44
2181 | 0 | 0 | 0 | 26.9 | 3.89
2182 | 0 | 0 | 0 | 26.1 | 1.67
2183 | 0 | 0 | 0 | 24.8 | 2.22
2184 | 0 | 0 | 0 | 23.7 | 0.56
2185 | 0 | 0 | 0 | 22.6 | 1.67
2186 | 0 | 0 | 0 | 22 | 1.67
2187 | 0 | 0 | 0 | 21.7 | 1.11
2188 | 0 | 0 | 0 | 21.1 | 1.39
2189 | 0 | 0 | 0 | 20.8 | 1.11
2190 | 94.4 | 36.1 | 362.1 | 20.7 | 0.28
2191 | 325 | 100 | 578.3 | 22.6 | 0.28
2192 | 550 | 136.1 | 679.9 | 26.1 | 1.11
2193 | 736.1 | 155.6 | 736.7 | 28 | 3.61
2194 | 852.8 | 161.1 | 756 | 29.5 | 3.33
2195 | 888.9 | 166.7 | 736.5 | 31.5 | 2.78
2196 | 858.3 | 169.4 | 702.5 | 32.7 | 1.67
2197 | 725 | 147.2 | 631.5 | 32.9 | 2.22
2198 | 611.1 | 152.8 | 581.6 | 33.6 | 2.78
2199 | 550 | 152.8 | 652.5 | 34.5 | 2.22
2200 | 338.9 | 108.3 | 592.6 | 34.1 | 2.22
2201 | 63.9 | 22.2 | 289.2 | 32.8 | 1.67
2202 | 5.6 | 0 | 0 | 30.2 | 2.22
2203 | 0 | 0 | 0 | 28.6 | 1.94
2204 | 0 | 0 | 0 | 27.9 | 3.89
2205 | 0 | 0 | 0 | 25.9 | 3.61
2206 | 0 | 0 | 0 | 24.5 | 2.78
2207 | 0 | 0 | 0 | 23.7 | 2.78
2208 | 0 | 0 | 0 | 22.8 | 0.83
2209 | 0 | 0 | 0 | 22.5 | 1.94
2210 | 0 | 0 | 0 | 21.7 | 0.83
2211 | 0 | 0 | 0 | 21.1 | 2.78
2212 | 0 | 0 | 0 | 20.6 | 2.22
2213 | 0 | 0 | 0 | 20.2 | 0.83
2214 | 94.4 | 36.1 | 366.2 | 20.2 | 1.11
2215 | 327.8 | 97.2 | 590.5 | 22.4 | 0.56
2216 | 572.2 | 119.4 | 742.3 | 25.3 | 2.22
2217 | 744.4 | 127.8 | 781.4 | 27.2 | 2.22
2218 | 852.8 | 147.2 | 770.3 | 28.8 | 2.22
2219 | 897.2 | 155.6 | 755.6 | 31.2 | 1.39
2220 | 925 | 133.3 | 806.5 | 33.1 | 2.78
2221 | 880.6 | 127.8 | 821.8 | 33.6 | 2.78
2222 | 769.4 | 122.2 | 820.1 | 33.6 | 3.89
2223 | 594.4 | 105.6 | 801.5 | 33.9 | 3.33
2224 | 369.4 | 77.8 | 742.4 | 33.4 | 3.89
2225 | 133.3 | 33.3 | 366.2 | 32.2 | 2.78
2226 | 2.8 | 0 | 0 | 29.4 | 2.5
2227 | 0 | 0 | 0 | 28.5 | 1.67
2228 | 0 | 0 | 0 | 27.4 | 3.89
2229 | 0 | 0 | 0 | 25.6 | 3.89
2230 | 0 | 0 | 0 | 24.6 | 3.06
2231 | 0 | 0 | 0 | 23.5 | 3.33
2232 | 0 | 0 | 0 | 22.4 | 1.11
2233 | 0 | 0 | 0 | 21 | 1.94
2234 | 0 | 0 | 0 | 21.3 | 1.94
2235 | 0 | 0 | 0 | 20.7 | 1.94
2236 | 0 | 0 | 0 | 19.9 | 3.33
2237 | 0 | 0 | 0 | 19.3 | 2.22
2238 | 86.1 | 36.1 | 340.1 | 19.5 | 2.22
2239 | 316.7 | 97.2 | 560.2 | 21.5 | 1.67
2240 | 533.3 | 144.4 | 636.3 | 24.2 | 2.78
2241 | 711.1 | 155.6 | 703 | 27.1 | 2.5
2242 | 830.6 | 166.7 | 724 | 29.2 | 2.5
2243 | 894.4 | 161.1 | 746.4 | 30.7 | 1.94
2244 | 900 | 161.1 | 752 | 32.2 | 2.22
2245 | 850 | 158.3 | 754.3 | 33.7 | 3.89
2246 | 727.8 | 155.6 | 724.1 | 34 | 2.78
2247 | 550 | 138.9 | 672.7 | 33.4 | 3.89
2248 | 311.1 | 108.3 | 517.6 | 32.9 | 3.33
2249 | 80.6 | 55.6 | 170 | 31.7 | 3.33
2250 | 0 | 2.8 | 0 | 29 | 4.17
2251 | 0 | 0 | 0 | 27.6 | 2.78
2252 | 0 | 0 | 0 | 26.8 | 2.78
2253 | 0 | 0 | 0 | 25.6 | 3.33
2254 | 0 | 0 | 0 | 24.1 | 3.89
2255 | 0 | 0 | 0 | 23 | 2.78
2256 | 0 | 0 | 0 | 21.9 | 1.39
2257 | 0 | 0 | 0 | 21.5 | 1.94
2258 | 0 | 0 | 0 | 20.6 | 2.78
2259 | 0 | 0 | 0 | 19.3 | 2.5
2260 | 0 | 0 | 0 | 18.8 | 1.11
2261 | 0 | 0 | 0 | 18.5 | 0.28
2262 | 100 | 38.9 | 374.4 | 19.2 | 1.39
2263 | 338.9 | 83.3 | 650.2 | 21.8 | 1.11
2264 | 566.7 | 111.1 | 744 | 25.5 | 1.39
2265 | 763.9 | 122.2 | 810.9 | 28.8 | 0.83
2266 | 894.4 | 122.2 | 841.3 | 30.6 | 2.78
2267 | 941.7 | 130.6 | 824.8 | 32.1 | 3.89
2268 | 922.2 | 141.7 | 793.7 | 33.2 | 3.89
2269 | 861.1 | 136.1 | 789.8 | 34.4 | 3.33
2270 | 733.3 | 133.3 | 758.2 | 34.6 | 3.33
2271 | 544.4 | 119.4 | 694.1 | 34.4 | 3.89
2272 | 311.1 | 94.4 | 551.3 | 33.5 | 2.78
2273 | 80.6 | 58.3 | 149.7 | 32.4 | 2.78
2274 | 0 | 2.8 | 0 | 30 | 3.89
2275 | 0 | 0 | 0 | 28.5 | 3.61
2276 | 0 | 0 | 0 | 26.4 | 3.89
2277 | 0 | 0 | 0 | 25.2 | 2.78
2278 | 0 | 0 | 0 | 23.9 | 2.78
2279 | 0 | 0 | 0 | 22.6 | 2.5
2280 | 0 | 0 | 0 | 22.6 | 1.67
2281 | 0 | 0 | 0 | 22.5 | 1.11
2282 | 0 | 0 | 0 | 21.3 | 1.94
2283 | 0 | 0 | 0 | 19.4 | 2.22
2284 | 0 | 0 | 0 | 18.7 | 1.11
2285 | 0 | 0 | 0 | 18.1 | 1.39
2286 | 102.8 | 30.6 | 378.4 | 18.5 | 1.94
2287 | 361.1 | 80.6 | 711.5 | 21 | 0.28
2288 | 588.9 | 108.3 | 783.4 | 24.1 | 2.22
2289 | 763.9 | 130.6 | 799.3 | 27.7 | 3.06
2290 | 897.2 | 136.1 | 828.4 | 29.4 | 2.78
2291 | 955.6 | 138.9 | 829.7 | 31.5 | 3.33
2292 | 966.7 | 136.1 | 843.8 | 33 | 3.61
2293 | 888.9 | 125 | 831.4 | 33.4 | 3.89
2294 | 783.3 | 100 | 862.5 | 33.5 | 3.33
2295 | 605.6 | 91.7 | 837.8 | 33.8 | 2.78
2296 | 388.9 | 72.2 | 745.5 | 33.1 | 2.78
2297 | 144.4 | 36.1 | 378.4 | 32 | 2.78
2298 | 0 | 0 | 0 | 29.5 | 2.78
2299 | 0 | 0 | 0 | 27.8 | 1.94
2300 | 0 | 0 | 0 | 26.7 | 2.22
2301 | 0 | 0 | 0 | 25.4 | 3.33
2302 | 0 | 0 | 0 | 24.6 | 2.78
2303 | 0 | 0 | 0 | 23.6 | 2.78
2304 | 0 | 0 | 0 | 23 | 1.94
2305 | 0 | 0 | 0 | 22.9 | 0.83
2306 | 0 | 0 | 0 | 22.4 | 1.94
2307 | 0 | 0 | 0 | 21.7 | 0.28
2308 | 0 | 0 | 0 | 21 | 1.39
2309 | 2.8 | 0 | 0 | 20.9 | 1.94
2310 | 111.1 | 27.8 | 382.3 | 20.8 | 1.11
2311 | 355.6 | 113.9 | 611 | 23.2 | 0
2312 | 566.7 | 150 | 678.1 | 25.3 | 1.94
2313 | 750 | 116.7 | 798.4 | 27.3 | 2.78
2314 | 872.2 | 116.7 | 821.5 | 29.4 | 1.11
2315 | 938.9 | 122.2 | 829 | 31.4 | 2.78
2316 | 961.1 | 111.1 | 862.8 | 33.3 | 3.06
2317 | 894.4 | 119.4 | 842.7 | 33.3 | 4.17
2318 | 719.4 | 116.7 | 759.9 | 34 | 4.72
2319 | 536.1 | 100 | 709.7 | 34 | 4.44
2320 | 316.7 | 80.6 | 596.9 | 33.3 | 2.78
2321 | 77.8 | 27.8 | 330.4 | 31.7 | 5.56
2322 | 0 | 0 | 0 | 29.9 | 3.89
2323 | 0 | 0 | 0 | 28.8 | 2.78
2324 | 0 | 0 | 0 | 27.7 | 3.06
2325 | 0 | 0 | 0 | 26.4 | 3.33
2326 | 0 | 0 | 0 | 24.8 | 2.78
2327 | 0 | 0 | 0 | 24 | 1.67
2328 | 0 | 0 | 0 | 23.2 | 2.22
2329 | 0 | 0 | 0 | 22.6 | 2.5
2330 | 0 | 0 | 0 | 22.4 | 0.28
2331 | 0 | 0 | 0 | 21.6 | 0.28
2332 | 0 | 0 | 0 | 20.9 | 0.83
2333 | 0 | 0 | 0 | 20 | 1.11
2334 | 125 | 38.9 | 386.2 | 20.5 | 1.39
2335 | 363.9 | 108.3 | 644.1 | 23.2 | 1.67
2336 | 580.6 | 144.4 | 708.5 | 26.1 | 2.78
2337 | 741.7 | 172.2 | 717 | 27.7 | 2.78
2338 | 855.6 | 194.4 | 718.2 | 30.1 | 2.78
2339 | 894.4 | 208.3 | 695.9 | 32.1 | 3.33
2340 | 902.8 | 200 | 712.9 | 33.1 | 3.33
2341 | 833.3 | 188.9 | 700.1 | 34.1 | 2.78
2342 | 688.9 | 175 | 647.1 | 33.6 | 3.33
2343 | 477.8 | 166.7 | 505.4 | 33.2 | 3.33
2344 | 255.6 | 116.7 | 350.1 | 32.1 | 3.33
2345 | 69.4 | 55.6 | 90.9 | 31.1 | 3.61
2346 | 0 | 0 | 0 | 29.3 | 3.61
2347 | 0 | 0 | 0 | 28.4 | 2.78
2348 | 0 | 0 | 0 | 27.4 | 3.33
2349 | 0 | 0 | 0 | 26 | 2.78
2350 | 0 | 0 | 0 | 25.1 | 1.94
2351 | 0 | 0 | 0 | 24 | 2.22
2352 | 0 | 0 | 0 | 23.2 | 2.5
2353 | 0 | 0 | 0 | 22.3 | 1.67
2354 | 0 | 0 | 0 | 21.9 | 1.39
2355 | 0 | 0 | 0 | 21.6 | 1.67
2356 | 0 | 0 | 0 | 21.6 | 1.11
2357 | 0 | 16.7 | 0 | 21.2 | 1.39
2358 | 83.3 | 66.7 | 108.1 | 21.8 | 1.67
2359 | 302.8 | 105.6 | 495.6 | 24 | 1.67
2360 | 536.1 | 125 | 666.8 | 26.1 | 4.44
2361 | 758.3 | 133.3 | 786.1 | 28.2 | 4.44
2362 | 847.2 | 155.6 | 750.8 | 30.4 | 3.89
2363 | 883.3 | 161.1 | 732 | 32.3 | 3.33
2364 | 827.8 | 150 | 687 | 33.6 | 3.33
2365 | 836.1 | 141.7 | 753.8 | 34.5 | 2.22
2366 | 716.7 | 127.8 | 740.7 | 35 | 3.61
2367 | 544.4 | 122.2 | 684.8 | 34.6 | 4.44
2368 | 311.1 | 102.8 | 523.5 | 34 | 3.89
2369 | 66.7 | 47.2 | 126.1 | 32.5 | 3.33
2370 | 0 | 0 | 0 | 30.4 | 4.44
2371 | 0 | 0 | 0 | 29.2 | 3.33
2372 | 0 | 0 | 0 | 28.4 | 3.06
2373 | 0 | 0 | 0 | 27.3 | 3.33
2374 | 0 | 0 | 0 | 26.1 | 2.22
2375 | 0 | 0 | 0 | 25.1 | 1.67
2376 | 0 | 0 | 0 | 24.6 | 2.78
2377 | 0 | 0 | 0 | 23.2 | 1.11
2378 | 0 | 0 | 0 | 23 | 2.78
2379 | 0 | 0 | 0 | 22.5 | 1.94
2380 | 0 | 0 | 0 | 22 | 1.39
2381 | 0 | 2.8 | 0 | 21.5 | 2.22
2382 | 119.4 | 16.7 | 393.6 | 21.6 | 2.5
2383 | 350 | 61.1 | 723.8 | 23 | 1.67
2384 | 561.1 | 127.8 | 701.7 | 26 | 4.44
2385 | 727.8 | 175 | 694.6 | 27.8 | 3.89
2386 | 836.1 | 200 | 689.9 | 30 | 3.89
2387 | 847.2 | 205.6 | 650 | 31.1 | 3.33
2388 | 811.1 | 225 | 593.7 | 33 | 1.94
2389 | 725 | 230.6 | 536.3 | 34.4 | 2.78
2390 | 655.6 | 208.3 | 561.9 | 34.6 | 5
2391 | 369.4 | 188.9 | 292.4 | 34.4 | 3.89
2392 | 236.1 | 133.3 | 257.5 | 33.6 | 3.33
2393 | 116.7 | 61.1 | 357.2 | 32 | 3.61
2394 | 5.6 | 0 | 0 | 30.3 | 4.44
2395 | 0 | 0 | 0 | 29.7 | 3.33
2396 | 0 | 0 | 0 | 28.7 | 5
2397 | 0 | 0 | 0 | 27.3 | 4.17
2398 | 0 | 0 | 0 | 26.3 | 2.78
2399 | 0 | 0 | 0 | 25.3 | 2.22
2400 | 0 | 0 | 0 | 24.7 | 3.06
2401 | 0 | 0 | 0 | 23.8 | 0.56
2402 | 0 | 0 | 0 | 23.4 | 0
2403 | 0 | 0 | 0 | 22.9 | 2.5
2404 | 0 | 0 | 0 | 22 | 0.56
2405 | 0 | 0 | 0 | 21.4 | 0
2406 | 41.7 | 55.6 | 0 | 22.2 | 0
2407 | 275 | 113.9 | 402.5 | 24.5 | 1.11
2408 | 530.6 | 158.3 | 601.8 | 27.3 | 1.94
2409 | 725 | 166.7 | 700.8 | 28.7 | 2.78
2410 | 833.3 | 191.7 | 695.5 | 31.2 | 3.06
2411 | 897.2 | 202.8 | 703 | 32.9 | 2.5
2412 | 891.7 | 194.4 | 705.8 | 34.5 | 2.22
2413 | 816.7 | 188.9 | 680.4 | 34.7 | 3.33
2414 | 697.2 | 180.6 | 648.5 | 34.3 | 3.33
2415 | 519.4 | 163.9 | 574.9 | 34.7 | 3.61
2416 | 238.9 | 130.6 | 270.7 | 34.2 | 2.78
2417 | 75 | 22.2 | 336.4 | 32.6 | 3.33
2418 | 0 | 0 | 0 | 30.5 | 4.44
2419 | 0 | 0 | 0 | 29.3 | 4.17
2420 | 0 | 0 | 0 | 27.9 | 4.44
2421 | 0 | 0 | 0 | 26.7 | 4.44
2422 | 0 | 0 | 0 | 25.5 | 3.33
2423 | 0 | 0 | 0 | 25.2 | 2.5
2424 | 0 | 0 | 0 | 24.6 | 3.33
2425 | 0 | 0 | 0 | 24.1 | 2.78
2426 | 0 | 0 | 0 | 22.5 | 2.78
2427 | 0 | 0 | 0 | 22.4 | 1.94
2428 | 0 | 0 | 0 | 21.7 | 1.94
2429 | 2.8 | 0 | 0 | 20.8 | 0
2430 | 97.2 | 61.1 | 228.2 | 21.5 | 1.11
2431 | 336.1 | 116.7 | 546.7 | 24.4 | 0.28
2432 | 544.4 | 144.4 | 645.8 | 27.4 | 2.22
2433 | 700 | 158.3 | 679.3 | 29.7 | 3.06
2434 | 844.4 | 183.3 | 716.1 | 32.5 | 2.78
2435 | 919.4 | 172.2 | 756 | 33 | 3.33
2436 | 916.7 | 163.9 | 761.6 | 33.6 | 4.44
2437 | 861.1 | 161.1 | 758.2 | 34.1 | 5.56
2438 | 744.4 | 161.1 | 731.5 | 34 | 5
2439 | 580.6 | 155.6 | 686.1 | 34.2 | 5
2440 | 369.4 | 127.8 | 602.1 | 33.7 | 3.89
2441 | 150 | 69.4 | 400.8 | 32.5 | 4.44
2442 | 2.8 | 2.8 | 0 | 30.4 | 4.17
2443 | 0 | 0 | 0 | 28.1 | 2.78
2444 | 0 | 0 | 0 | 26.6 | 2.5
2445 | 0 | 0 | 0 | 25.8 | 1.94
2446 | 0 | 0 | 0 | 25 | 2.22
2447 | 0 | 0 | 0 | 24.7 | 1.11
2448 | 0 | 0 | 0 | 23.4 | 3.61
2449 | 0 | 0 | 0 | 22.5 | 1.86
2450 | 0 | 0 | 0 | 21.9 | 1.87
2451 | 0 | 0 | 0 | 21.7 | 1.99
2452 | 0 | 0 | 0 | 21.4 | 1.84
2453 | 5.6 | 0 | 0 | 21.2 | 1.41
2454 | 175 | 0 | 404.3 | 21.7 | 1.46
2455 | 369.4 | 52.8 | 751.8 | 23.7 | 1.55
2456 | 563.9 | 119.4 | 716.5 | 26.4 | 2.61
2457 | 725 | 152.8 | 717 | 28.2 | 2.86
2458 | 811.1 | 161.1 | 703.6 | 30.3 | 2.66
2459 | 855.6 | 166.7 | 696.6 | 32.6 | 2.61
2460 | 905.6 | 169.4 | 744.3 | 33.7 | 2.6
2461 | 841.7 | 163.9 | 733.6 | 34.9 | 2.86
2462 | 744.4 | 155.6 | 737.9 | 35.3 | 3.04
2463 | 591.7 | 133.3 | 738.9 | 35 | 3.06
2464 | 394.4 | 83.3 | 751.8 | 33.9 | 2.97
2465 | 144.4 | 11.1 | 404.3 | 32.4 | 3.12
2466 | 11.1 | 0 | 0 | 29.6 | 2.93
2467 | 0 | 0 | 0 | 28.6 | 2.69
2468 | 0 | 0 | 0 | 27.1 | 2.98
2469 | 0 | 0 | 0 | 25.6 | 3.03
2470 | 0 | 0 | 0 | 24.8 | 2.51
2471 | 0 | 0 | 0 | 24.1 | 2.48
2472 | 0 | 0 | 0 | 24.04 | 3.89
2473 | 0 | 0 | 0 | 23.33 | 2.78
2474 | 0 | 0 | 0 | 22.69 | 2.5
2475 | 0 | 0 | 0 | 22.17 | 1.39
2476 | 0 | 0 | 0 | 21.75 | 2.22
2477 | 2.8 | 0 | 0 | 21.29 | 0.56
2478 | 108.3 | 69.4 | 241.7 | 21.61 | 1.11
2479 | 263.9 | 177.8 | 213.4 | 23.72 | 1.67
2480 | 602.8 | 191.7 | 661.9 | 26.08 | 3.89
2481 | 766.7 | 161.1 | 758.1 | 28.12 | 3.89
2482 | 861.1 | 163.9 | 754.2 | 30.09 | 2.78
2483 | 925 | 161.1 | 772.1 | 31.83 | 2.22
2484 | 936.1 | 150 | 794.5 | 33.11 | 1.39
2485 | 880.6 | 152.8 | 787.3 | 33.78 | 3.33
2486 | 758.3 | 133.3 | 782.4 | 34.05 | 3.89
2487 | 561.1 | 113.9 | 720 | 33.97 | 3.89
2488 | 338.9 | 58.3 | 695.2 | 33.06 | 3.33
2489 | 94.4 | 8.3 | 407.7 | 31.35 | 3.89
2490 | 0 | 0 | 0 | 29.58 | 2.78
2491 | 0 | 0 | 0 | 28.46 | 2.78
2492 | 0 | 0 | 0 | 27.39 | 1.11
2493 | 0 | 0 | 0 | 26.43 | 2.22
2494 | 0 | 0 | 0 | 25.48 | 1.67
2495 | 0 | 0 | 0 | 24.56 | 0.56
2496 | 0 | 0 | 0 | 23.7 | 4.17
2497 | 0 | 0 | 0 | 23 | 1.67
2498 | 0 | 0 | 0 | 21.5 | 0.56
2499 | 0 | 0 | 0 | 21.9 | 1.94
2500 | 0 | 0 | 0 | 21.8 | 1.11
2501 | 5.6 | 11.1 | 0 | 21.3 | 1.11
2502 | 144.4 | 80.6 | 393.9 | 21.8 | 0
2503 | 380.6 | 130.6 | 617.9 | 24.1 | 0.28
2504 | 588.9 | 141.7 | 719.1 | 25.8 | 2.78
2505 | 747.2 | 150 | 747.1 | 27.7 | 2.22
2506 | 852.8 | 166.7 | 741.8 | 29.3 | 2.78
2507 | 897.2 | 186.1 | 718.4 | 31.6 | 2.78
2508 | 911.1 | 166.7 | 752.1 | 33 | 1.94
2509 | 852.8 | 163.9 | 744.8 | 34.1 | 1.67
2510 | 736.1 | 150 | 733.2 | 34.6 | 2.78
2511 | 536.1 | 125 | 661 | 34.3 | 5
2512 | 297.2 | 94.4 | 501.2 | 33.9 | 4.44
2513 | 72.2 | 41.7 | 188.4 | 32.8 | 4.17
2514 | 0 | 0 | 0 | 30.2 | 3.33
2515 | 0 | 0 | 0 | 29.5 | 1.11
2516 | 0 | 0 | 0 | 28 | 1.11
2517 | 0 | 0 | 0 | 26.6 | 1.67
2518 | 0 | 0 | 0 | 25.5 | 2.22
2519 | 0 | 0 | 0 | 24.7 | 1.67
2520 | 0 | 0 | 0 | 24.4 | 4.44
2521 | 0 | 0 | 0 | 22.8 | 0.56
2522 | 0 | 0 | 0 | 21.8 | 0.56
2523 | 0 | 0 | 0 | 21.3 | 0.83
2524 | 0 | 0 | 0 | 21.4 | 1.67
2525 | 2.8 | 13.9 | 0 | 20.7 | 0.28
2526 | 66.7 | 155.6 | 0 | 21.2 | 0.28
2527 | 280.6 | 202.8 | 191.7 | 24 | 1.67
2528 | 461.1 | 197.2 | 423.8 | 24.6 | 2.78
2529 | 716.7 | 216.7 | 625 | 26.6 | 2.78
2530 | 816.7 | 238.9 | 624.4 | 28.7 | 3.89
2531 | 861.1 | 250 | 617.1 | 31.2 | 2.78
2532 | 900 | 230.6 | 676 | 33.1 | 2.78
2533 | 844.4 | 219.4 | 675.4 | 34.1 | 3.33
2534 | 683.3 | 255.6 | 534.7 | 34.2 | 2.78
2535 | 530.6 | 197.2 | 535.3 | 34.2 | 4.17
2536 | 294.4 | 141.7 | 376.6 | 33.6 | 4.17
2537 | 102.8 | 52.8 | 305.9 | 32.4 | 5
2538 | 2.8 | 0 | 0 | 30.3 | 3.06
2539 | 0 | 0 | 0 | 28.6 | 3.33
2540 | 0 | 0 | 0 | 28.2 | 3.33
2541 | 0 | 0 | 0 | 27.2 | 3.06
2542 | 0 | 0 | 0 | 26.3 | 3.06
2543 | 0 | 0 | 0 | 25.1 | 3.61
2544 | 0 | 0 | 0 | 24.4 | 4.72
2545 | 0 | 0 | 0 | 23.9 | 3.06
2546 | 0 | 0 | 0 | 23.3 | 4.44
2547 | 0 | 0 | 0 | 22.7 | 4.44
2548 | 0 | 0 | 0 | 21.9 | 3.33
2549 | 19.4 | 0 | 0 | 22.5 | 3.89
2550 | 63.9 | 11.1 | 320.4 | 22.9 | 4.72
2551 | 205.6 | 111.1 | 232.3 | 24.8 | 3.33
2552 | 554 | 157 | 639.7 | 26.2 | 2.78
2553 | 739.2 | 167.6 | 717.5 | 28.3 | 3.89
2554 | 848 | 178.5 | 726.3 | 30.8 | 2.78
2555 | 882.4 | 196.6 | 694.1 | 32.5 | 3.33
2556 | 777.8 | 325 | 457.1 | 33.9 | 2.78
2557 | 525 | 391.7 | 144 | 34.8 | 2.78
2558 | 522.2 | 336.1 | 232.5 | 35.1 | 2.78
2559 | 405.6 | 263.9 | 227.2 | 35.5 | 1.67
2560 | 300 | 166.7 | 327.9 | 35.2 | 1.39
2561 | 77.8 | 47.2 | 185.5 | 34.3 | 0.56
2562 | 0 | 0 | 0 | 32.2 | 1.94
2563 | 0 | 0 | 0 | 31.4 | 2.22
2564 | 0 | 0 | 0 | 30.4 | 2.78
2565 | 0 | 0 | 0 | 29 | 1.67
2566 | 0 | 0 | 0 | 28.5 | 2.78
2567 | 0 | 0 | 0 | 26.4 | 3.61
2568 | 0 | 0 | 0 | 25.8 | 5
2569 | 0 | 0 | 0 | 24.7 | 4.17
2570 | 0 | 0 | 0 | 24.2 | 3.89
2571 | 0 | 0 | 0 | 23.6 | 4.44
2572 | 0 | 0 | 0 | 23.1 | 2.78
2573 | 27.8 | 0 | 0 | 22.9 | 3.33
2574 | 163.9 | 47.2 | 420.7 | 23.1 | 3.33
2575 | 336.1 | 122.2 | 524.8 | 24.6 | 4.17
2576 | 558.3 | 147.2 | 658.6 | 27.2 | 3.89
2577 | 739.2 | 188.9 | 717.5 | 28.9 | 3.33
2578 | 848 | 202.8 | 726.3 | 31.1 | 3.33
2579 | 900 | 208.3 | 698 | 32.8 | 3.33
2580 | 908.3 | 302.8 | 611.1 | 33.8 | 2.22
2581 | 805.6 | 375 | 464.9 | 34.7 | 1.67
2582 | 555.6 | 247.2 | 384.9 | 35.2 | 2.78
2583 | 630.6 | 225 | 649.7 | 35.1 | 2.78
2584 | 358.3 | 180.6 | 436.2 | 35.2 | 2.78
2585 | 75 | 52.8 | 133.9 | 30.1 | 1.11
2586 | 0 | 0 | 0 | 29 | 5
2587 | 0 | 0 | 0 | 28.7 | 2.22
2588 | 0 | 0 | 0 | 27 | 1.67
2589 | 0 | 0 | 0 | 27.5 | 5
2590 | 0 | 0 | 0 | 25 | 0.83
2591 | 0 | 0 | 0 | 24.4 | 5.56
2592 | 0 | 0 | 0 | 24.3 | 5.28
2593 | 0 | 0 | 0 | 24.6 | 2.78
2594 | 0 | 0 | 0 | 24.2 | 2.78
2595 | 0 | 0 | 0 | 24.3 | 2.22
2596 | 0 | 0 | 0 | 24 | 1.94
2597 | 0 | 0 | 0 | 22.4 | 0.28
2598 | 80.6 | 55.6 | 149.5 | 22.5 | 1.67
2599 | 333.3 | 111.1 | 543.9 | 25 | 0.83
2600 | 538.9 | 125 | 662.3 | 27.4 | 2.78
2601 | 705.6 | 152.8 | 689.6 | 29.4 | 1.39
2602 | 791.7 | 183.3 | 656.6 | 31.7 | 1.67
2603 | 830.6 | 191.7 | 644.6 | 32.9 | 2.22
2604 | 869.4 | 175 | 700.6 | 34.4 | 2.22
2605 | 880.6 | 202.8 | 731.6 | 34.4 | 2.22
2606 | 741.7 | 222.2 | 648 | 35.7 | 2.22
2607 | 572.2 | 250 | 515.6 | 35.2 | 2.78
2608 | 250 | 113.9 | 333.2 | 34.3 | 3.33
2609 | 47.2 | 19.4 | 166.1 | 28.8 | 3.61
2610 | 2.8 | 0 | 0 | 29 | 1.11
2611 | 0 | 0 | 0 | 29.1 | 3.33
2612 | 0 | 0 | 0 | 28.6 | 3.33
2613 | 0 | 0 | 0 | 27.9 | 3.61
2614 | 0 | 0 | 0 | 27.4 | 3.33
2615 | 0 | 0 | 0 | 26.3 | 3.33
2616 | 0 | 0 | 0 | 25.3 | 5.56
2617 | 0 | 0 | 0 | 24.4 | 2.22
2618 | 0 | 0 | 0 | 23.7 | 2.22
2619 | 0 | 0 | 0 | 23.1 | 2.22
2620 | 0 | 0 | 0 | 22.8 | 1.67
2621 | 2.8 | 5.6 | 0 | 22.3 | 2.78
2622 | 127.8 | 77.8 | 296.8 | 22.4 | 1.67
2623 | 308.3 | 175 | 325.6 | 23.9 | 2.78
2624 | 497.2 | 311.1 | 297.5 | 25.4 | 3.33
2625 | 741.7 | 336.1 | 505.7 | 27.4 | 3.06
2626 | 847.2 | 222.2 | 674.4 | 29.6 | 2.78
2627 | 891.7 | 202.8 | 694.9 | 31.4 | 2.78
2628 | 875 | 163.9 | 717.3 | 33.2 | 2.78
2629 | 725 | 188.9 | 578.5 | 33.4 | 3.33
2630 | 727.8 | 136.1 | 737.7 | 33.7 | 3.04
2631 | 586.1 | 150 | 697.1 | 34.2 | 3.06
2632 | 355.6 | 97.2 | 630.9 | 33.5 | 2.97
2633 | 125 | 44.4 | 426.8 | 32.5 | 3.33
2634 | 0 | 2.8 | 0 | 30.6 | 2.78
2635 | 0 | 0 | 0 | 29.8 | 2.78
2636 | 0 | 0 | 0 | 29.1 | 2.78
2637 | 0 | 0 | 0 | 28 | 2.78
2638 | 0 | 0 | 0 | 27.1 | 2.78
2639 | 0 | 0 | 0 | 25.8 | 3.33
2640 | 0 | 0 | 0 | 25.3 | 5.83
2641 | 0 | 0 | 0 | 25.1 | 2.78
2642 | 0 | 0 | 0 | 24.4 | 1.67
2643 | 0 | 0 | 0 | 23.9 | 0.56
2644 | 0 | 0 | 0 | 23.8 | 0.28
2645 | 2.8 | 0 | 0 | 22.8 | 0
2646 | 44.4 | 50 | 0 | 22.8 | 0.83
2647 | 291.7 | 88.9 | 494.1 | 25.4 | 2.78
2648 | 544.4 | 127.8 | 665.4 | 26.9 | 3.33
2649 | 730.6 | 141.7 | 733.9 | 28.8 | 5
2650 | 825 | 119.4 | 761.1 | 30.5 | 3.33
2651 | 927.8 | 125 | 809.6 | 31.5 | 3.61
2652 | 930.6 | 130.6 | 806.8 | 32.9 | 3.33
2653 | 869.4 | 122.2 | 806 | 33.3 | 3.33
2654 | 733.3 | 122.2 | 761.6 | 33.4 | 3.33
2655 | 544.4 | 113.9 | 687.6 | 33.3 | 2.5
2656 | 291.7 | 91.7 | 487.4 | 33.4 | 2.78
2657 | 66.7 | 47.2 | 114.6 | 31.9 | 2.78
2658 | 0 | 0 | 0 | 30.4 | 1.67
2659 | 0 | 0 | 0 | 29.4 | 2.78
2660 | 0 | 0 | 0 | 28.6 | 2.78
2661 | 0 | 0 | 0 | 27.7 | 2.78
2662 | 0 | 0 | 0 | 27.1 | 2.22
2663 | 0 | 0 | 0 | 26.5 | 2.78
2664 | 0 | 0 | 0 | 25.7 | 6.11
2665 | 0 | 0 | 0 | 24.7 | 1.67
2666 | 0 | 0 | 0 | 23.9 | 2.22
2667 | 0 | 0 | 0 | 23.3 | 2.22
2668 | 0 | 0 | 0 | 22.8 | 1.94
2669 | 8.3 | 8.3 | 0 | 22.4 | 1.11
2670 | 141.7 | 80.6 | 357.7 | 22.5 | 1.11
2671 | 355.6 | 125 | 560.6 | 24 | 1.11
2672 | 552.8 | 191.7 | 576.1 | 26.5 | 1.11
2673 | 739.2 | 167.6 | 717.5 | 28.6 | 1.94
2674 | 848 | 178.5 | 726.3 | 30.1 | 2.22
2675 | 894.4 | 227.8 | 672.3 | 31.5 | 2.22
2676 | 716.7 | 305.6 | 414.6 | 33.1 | 1.67
2677 | 513.9 | 330.6 | 197.7 | 33 | 3.89
2678 | 236.1 | 233.3 | 3.5 | 33 | 3.33
2679 | 263.9 | 225 | 62 | 33.5 | 3.89
2680 | 63.9 | 63.9 | 0 | 32.1 | 3.89
2681 | 61.1 | 58.3 | 16.3 | 29.4 | 2.78
2682 | 2.8 | 0 | 0 | 29.5 | 1.67
2683 | 0 | 0 | 0 | 28.8 | 5.56
2684 | 0 | 0 | 0 | 27.7 | 3.33
2685 | 0 | 0 | 0 | 26.8 | 3.33
2686 | 0 | 0 | 0 | 26.4 | 3.33
2687 | 0 | 0 | 0 | 25.8 | 3.89
2688 | 0 | 0 | 0 | 24.9 | 6.39
2689 | 0 | 0 | 0 | 24.1 | 2.78
2690 | 0 | 0 | 0 | 23.7 | 2.78
2691 | 0 | 0 | 0 | 23.6 | 1.99
2692 | 0 | 0 | 0 | 23.8 | 1.84
2693 | 8.3 | 0 | 0 | 23.8 | 1.11
2694 | 122.2 | 36.1 | 435.5 | 24 | 1.11
2695 | 372.2 | 86.1 | 694.3 | 25 | 1.11
2696 | 588.9 | 100 | 779.3 | 26.6 | 1.67
2697 | 747.2 | 122.2 | 778.2 | 28.7 | 1.11
2698 | 850 | 141.7 | 763.7 | 29.5 | 1.67
2699 | 850 | 225 | 630.2 | 31.7 | 2.78
2700 | 522.2 | 319.4 | 204.5 | 31.9 | 2.22
2701 | 200 | 197.2 | 3 | 32.8 | 1.94
2702 | 241.7 | 238.9 | 3.5 | 32.8 | 2.22
2703 | 119.4 | 108.3 | 17.7 | 30.2 | 1.39
2704 | 105.6 | 94.4 | 27 | 30.4 | 1.11
2705 | 69.4 | 77.8 | 0 | 30.4 | 0.28
2706 | 0 | 2.8 | 0 | 29.2 | 0
2707 | 0 | 0 | 0 | 28.1 | 2.22
2708 | 0 | 0 | 0 | 27 | 1.11
2709 | 0 | 0 | 0 | 26.2 | 0.56
2710 | 0 | 0 | 0 | 25 | 0
2711 | 0 | 0 | 0 | 25 | 1.67
2712 | 0 | 0 | 0 | 24.04 | 6.67
2713 | 0 | 0 | 0 | 23.33 | 1.11
2714 | 0 | 0 | 0 | 22.69 | 0
2715 | 0 | 0 | 0 | 22.17 | 0.56
2716 | 0 | 0 | 0 | 21.75 | 0
2717 | 13.9 | 13.9 | 0 | 21.29 | 0.56
2718 | 152.8 | 66.7 | 438.2 | 21.61 | 2.22
2719 | 361.1 | 102.8 | 625.6 | 23.72 | 2.78
2720 | 550 | 138.9 | 654.7 | 26.08 | 3.33
2721 | 727.8 | 144.4 | 726 | 28.12 | 3.33
2722 | 838.9 | 161.1 | 730.7 | 30.09 | 3.33
2723 | 852.8 | 197.2 | 660.9 | 31.83 | 2.78
2724 | 694.4 | 263.9 | 434.1 | 33.11 | 2.22
2725 | 466.7 | 286.1 | 194.6 | 33.78 | 1.94
2726 | 483.3 | 277.8 | 255.8 | 34.05 | 2.22
2727 | 144.4 | 158.3 | 0 | 33.97 | 1.67
2728 | 41.7 | 61.1 | 0 | 33.06 | 3.33
2729 | 13.9 | 36.1 | 0 | 31.35 | 2.22
2730 | 0 | 2.8 | 0 | 30.5 | 1.39
2731 | 0 | 0 | 0 | 28.6 | 0.56
2732 | 0 | 0 | 0 | 28.1 | 1.67
2733 | 0 | 0 | 0 | 28 | 0.83
2734 | 0 | 0 | 0 | 28.1 | 0.83
2735 | 0 | 0 | 0 | 26.8 | 0.56
2736 | 0 | 0 | 0 | 24.04 | 6.94
2737 | 0 | 0 | 0 | 23.33 | 0.28
2738 | 0 | 0 | 0 | 22.69 | 1.11
2739 | 0 | 0 | 0 | 22.17 | 1.67
2740 | 0 | 0 | 0 | 21.75 | 2.22
2741 | 0 | 16.7 | 0 | 21.29 | 1.94
2742 | 102.8 | 91.7 | 63.8 | 21.61 | 1.11
2743 | 330.6 | 141.7 | 456.5 | 23.72 | 1.94
2744 | 572.2 | 177.8 | 627.7 | 26.08 | 3.33
2745 | 741.7 | 186.1 | 691.2 | 28.12 | 1.67
2746 | 797.2 | 266.7 | 571.9 | 30.09 | 1.67
2747 | 816.7 | 308.3 | 512.5 | 31.83 | 0.56
2748 | 672.2 | 291.7 | 383.7 | 33.11 | 1.67
2749 | 594.4 | 277.8 | 341.3 | 33.78 | 0.83
2750 | 358.3 | 236.1 | 152.1 | 34.05 | 1.11
2751 | 263.9 | 216.7 | 75.1 | 33.97 | 1.67
2752 | 83.3 | 122.2 | 0 | 33.06 | 1.67
2753 | 22.2 | 16.7 | 31.9 | 31.35 | 2.78
2754 | 0 | 0 | 0 | 28.4 | 2.22
2755 | 0 | 0 | 0 | 27.2 | 4.44
2756 | 0 | 0 | 0 | 28.1 | 2.5
2757 | 0 | 0 | 0 | 27.8 | 3.89
2758 | 0 | 0 | 0 | 26.9 | 3.89
2759 | 0 | 0 | 0 | 26 | 3.33
2760 | 0 | 0 | 0 | 25.2 | 7.22
2761 | 0 | 0 | 0 | 24.3 | 3.33
2762 | 0 | 0 | 0 | 23.5 | 3.06
2763 | 0 | 0 | 0 | 22.9 | 3.33
2764 | 0 | 0 | 0 | 22.4 | 2.78
2765 | 0 | 0 | 0 | 21.9 | 2.5
2766 | 86.1 | 77.8 | 47.5 | 22.4 | 1.11
2767 | 269.4 | 183.3 | 207.7 | 24.2 | 0.56
2768 | 483.3 | 241.7 | 384.3 | 26.8 | 1.11
2769 | 688.9 | 211.1 | 594.3 | 28.3 | 1.94
2770 | 863.9 | 186.1 | 730.5 | 30.6 | 1.94
2771 | 905.6 | 180.6 | 730.9 | 32.5 | 1.11
2772 | 900 | 183.3 | 722.5 | 33.4 | 2.22
2773 | 805.6 | 155.6 | 700.6 | 33.9 | 3.33
2774 | 719.4 | 138.9 | 722.1 | 34.8 | 3.89
2775 | 536.1 | 147.2 | 618.3 | 33.97 | 3.89
2776 | 233.3 | 138.9 | 227.8 | 33 | 3.33
2777 | 33.3 | 77.8 | 0 | 31.9 | 3.33
2778 | 0 | 5.6 | 0 | 30.6 | 2.78
2779 | 0 | 0 | 0 | 29.6 | 2.78
2780 | 0 | 0 | 0 | 28.7 | 2.78
2781 | 0 | 0 | 0 | 28 | 2.78
2782 | 0 | 0 | 0 | 27.1 | 3.89
2783 | 0 | 0 | 0 | 26.5 | 1.94
2784 | 0 | 0 | 0 | 25.6 | 7.5
2785 | 0 | 0 | 0 | 24.8 | 1.67
2786 | 0 | 0 | 0 | 24.5 | 1.39
2787 | 0 | 0 | 0 | 23.7 | 2.78
2788 | 0 | 0 | 0 | 23.3 | 1.94
2789 | 22.2 | 8.3 | 0 | 23 | 0
2790 | 177.8 | 66.7 | 446.1 | 23.2 | 0.28
2791 | 386.1 | 111.1 | 662.2 | 25.6 | 2.22
2792 | 569.4 | 136.1 | 688.5 | 27.7 | 3.33
2793 | 702.8 | 166.7 | 666.6 | 29.3 | 3.89
2794 | 841.7 | 191.7 | 700.6 | 30.6 | 2.78
2795 | 911.1 | 244.4 | 672.2 | 32.6 | 2.78
2796 | 850 | 352.8 | 501.3 | 33.3 | 2.78
2797 | 625 | 341.7 | 305.4 | 33.9 | 2.22
2798 | 375 | 275 | 124.3 | 34.6 | 1.11
2799 | 386.1 | 311.1 | 119.2 | 33.97 | 1.94
2800 | 122.2 | 152.8 | 0 | 31.8 | 2.78
2801 | 25 | 55.6 | 0 | 30.8 | 3.89
2802 | 8.3 | 8.3 | 0 | 30.5 | 2.78
2803 | 0 | 0 | 0 | 26.7 | 1.94
2804 | 0 | 0 | 0 | 22.5 | 4.44
2805 | 0 | 0 | 0 | 23.5 | 4.44
2806 | 0 | 0 | 0 | 24.1 | 2.22
2807 | 0 | 0 | 0 | 21.6 | 3.33
2808 | 0 | 0 | 0 | 22.2 | 7.78
2809 | 0 | 0 | 0 | 22.1 | 0
2810 | 0 | 0 | 0 | 21.3 | 1.67
2811 | 0 | 0 | 0 | 20.9 | 3.33
2812 | 0 | 0 | 0 | 20.5 | 5.56
2813 | 0 | 5.6 | 0 | 20.3 | 4.44
2814 | 88.9 | 63.9 | 140.8 | 20.7 | 2.22
2815 | 358.3 | 122.2 | 567.6 | 22.9 | 1.67
2816 | 583.3 | 122.2 | 732.1 | 25.8 | 2.22
2817 | 833.3 | 130.6 | 873.7 | 27.6 | 3.33
2818 | 938.9 | 127.8 | 874.2 | 30 | 2.78
2819 | 997.2 | 158.3 | 845.9 | 31 | 2.22
2820 | 927.8 | 244.4 | 689 | 32.2 | 2.22
2821 | 830.6 | 216.7 | 661.6 | 32.1 | 1.94
2822 | 761.1 | 250 | 635.4 | 33 | 1.67
2823 | 583.3 | 150 | 688 | 32.8 | 1.94
2824 | 236.1 | 122.2 | 273.8 | 28 | 2.78
2825 | 91.7 | 52.8 | 219.1 | 26.9 | 4.72
2826 | 8.3 | 0 | 0 | 26.5 | 2.22
2827 | 0 | 0 | 0 | 26.7 | 1.67
2828 | 0 | 0 | 0 | 26 | 1.94
2829 | 0 | 0 | 0 | 24 | 3.89
2830 | 0 | 0 | 0 | 23.3 | 4.44
2831 | 0 | 0 | 0 | 23 | 1.67
2832 | 0 | 0 | 0 | 22.8 | 8.06
2833 | 0 | 0 | 0 | 22.4 | 1.67
2834 | 0 | 0 | 0 | 22 | 2.22
2835 | 0 | 0 | 0 | 21.7 | 2.22
2836 | 0 | 0 | 0 | 21.7 | 1.67
2837 | 0 | 0 | 0 | 21.4 | 0.56
2838 | 61.1 | 11.1 | 280 | 22 | 1.11
2839 | 288.9 | 119.4 | 406.6 | 23.8 | 1.39
2840 | 513.9 | 216.7 | 471.6 | 26.4 | 1.67
2841 | 675 | 241.7 | 538.6 | 28.2 | 2.78
2842 | 805.6 | 244.4 | 604.7 | 29.8 | 2.5
2843 | 800 | 269.4 | 535 | 30.9 | 2.22
2844 | 641.7 | 319.4 | 324.9 | 32 | 2.78
2845 | 363.9 | 277.8 | 92.8 | 33.2 | 2.22
2846 | 133.3 | 150 | 0 | 32.9 | 2.22
2847 | 69.4 | 86.1 | 0 | 33 | 2.22
2848 | 219.4 | 227.8 | 0 | 29.6 | 1.94
2849 | 52.8 | 97.2 | 0 | 24.2 | 3.89
2850 | 2.8 | 2.8 | 0 | 25.2 | 5.83
2851 | 0 | 0 | 0 | 24.6 | 1.11
2852 | 0 | 0 | 0 | 23.6 | 5
2853 | 0 | 0 | 0 | 23.7 | 2.78
2854 | 0 | 0 | 0 | 23.7 | 1.67
2855 | 0 | 0 | 0 | 23 | 1.67
2856 | 0 | 0 | 0 | 24.04 | 8.33
2857 | 0 | 0 | 0 | 23.33 | 1.94
2858 | 0 | 0 | 0 | 22.69 | 0.83
2859 | 0 | 0 | 0 | 22.17 | 1.11
2860 | 0 | 0 | 0 | 21.75 | 2.22
2861 | 0 | 0 | 0 | 21.29 | 2.22
2862 | 38.9 | 47.2 | 0 | 21.61 | 2.78
2863 | 227.8 | 183.3 | 106.5 | 23.72 | 3.89
2864 | 597.2 | 225 | 590.2 | 26.08 | 3.89
2865 | 827.8 | 202.8 | 776.7 | 28.12 | 3.89
2866 | 869.4 | 263.9 | 652.7 | 30.09 | 2.22
2867 | 705.6 | 411.1 | 297 | 31.83 | 2.22
2868 | 569.4 | 369.4 | 201.7 | 33.11 | 2.22
2869 | 247.2 | 219.4 | 29.9 | 33.78 | 3.33
2870 | 269.4 | 211.1 | 72.5 | 34.05 | 2.78
2871 | 227.8 | 205.6 | 35.2 | 33.97 | 2.22
2872 | 91.7 | 105.6 | 0 | 33.06 | 2.22
2873 | 25 | 30.6 | 0 | 31.35 | 2.78
2874 | 0 | 0 | 0 | 25.7 | 2.22
2875 | 0 | 0 | 0 | 25.4 | 2.22
2876 | 0 | 0 | 0 | 25.9 | 2.22
2877 | 0 | 0 | 0 | 24.8 | 1.67
2878 | 0 | 0 | 0 | 21.9 | 1.39
2879 | 0 | 0 | 0 | 21.7 | 1.67
2880 | 0 | 0 | 0 | 22 | 0.28
2881 | 0 | 0 | 0 | 22 | 1.39
2882 | 0 | 0 | 0 | 22.2 | 0
2883 | 0 | 0 | 0 | 22.8 | 0
2884 | 0 | 0 | 0 | 22.5 | 1.11
2885 | 22.2 | 0 | 0 | 22.3 | 1.39
2886 | 169.4 | 55.6 | 415.1 | 22.6 | 1.67
2887 | 313.9 | 155.6 | 378.7 | 23.5 | 1.11
2888 | 461.1 | 277.8 | 290.5 | 25.4 | 2.22
2889 | 391.7 | 336.1 | 69 | 26.4 | 2.78
2890 | 627.8 | 427.8 | 215.6 | 27.6 | 2.22
2891 | 641.7 | 433.3 | 210.1 | 28.8 | 2.22
2892 | 658.3 | 377.8 | 283 | 30.2 | 1.11
2893 | 641.7 | 372.2 | 290.4 | 31.4 | 1.11
2894 | 788.9 | 286.1 | 624.7 | 31.2 | 2.5
2895 | 516.7 | 252.8 | 418.2 | 31.1 | 2.78
2896 | 330.6 | 197.2 | 318.9 | 30.4 | 2.78
2897 | 69.4 | 55.6 | 76.9 | 29.6 | 3.06
2898 | 0 | 0 | 0 | 28.3 | 3.89
2899 | 0 | 0 | 0 | 27.4 | 1.39
2900 | 0 | 0 | 0 | 26.8 | 2.22
2901 | 0 | 0 | 0 | 26.3 | 1.11
2902 | 0 | 0 | 0 | 25.8 | 1.67
2903 | 0 | 0 | 0 | 25.3 | 2.22
2904 | 0 | 0 | 0 | 24.7 | 0.56
2905 | 0 | 0 | 0 | 24 | 4.17
2906 | 0 | 0 | 0 | 23.7 | 2.78
2907 | 0 | 0 | 0 | 23.7 | 1.94
2908 | 0 | 0 | 0 | 23.2 | 2.22
2909 | 0 | 13.9 | 0 | 22.9 | 1.67
2910 | 97.2 | 119.4 | 0 | 23.4 | 1.11
2911 | 366.7 | 202.8 | 391.4 | 24.5 | 1.11
2912 | 558.3 | 252.8 | 484 | 26.5 | 1.67
2913 | 750 | 322.2 | 531.5 | 28.1 | 1.67
2914 | 750 | 444.4 | 329.4 | 28.6 | 2.22
2915 | 686.1 | 513.9 | 173.8 | 30.5 | 0.83
2916 | 941.7 | 480.6 | 465.2 | 31 | 1.11
2917 | 597.2 | 425 | 185.7 | 31.7 | 1.67
2918 | 361.1 | 358.3 | 3.5 | 31.4 | 2.78
2919 | 338.9 | 272.2 | 105.6 | 31.5 | 3.33
2920 | 225 | 155.6 | 165.8 | 31.4 | 2.78
2921 | 41.7 | 55.6 | 0 | 30.3 | 1.11
2922 | 0 | 2.8 | 0 | 22.5 | 1.39
2923 | 0 | 0 | 0 | 21.9 | 9.44
2924 | 0 | 0 | 0 | 23.3 | 3.33
2925 | 0 | 0 | 0 | 23.4 | 3.33
2926 | 0 | 0 | 0 | 21.9 | 1.67
2927 | 0 | 0 | 0 | 21.6 | 2.22
2928 | 0 | 0 | 0 | 21.5 | 0.83
2929 | 0 | 0 | 0 | 21.5 | 0
2930 | 0 | 0 | 0 | 21.5 | 0
2931 | 0 | 0 | 0 | 21.6 | 1.11
2932 | 0 | 0 | 0 | 21.7 | 1.39
2933 | 0 | 5.6 | 0 | 21.9 | 0.56
2934 | 58.3 | 77.8 | 0 | 22.4 | 0.56
2935 | 269.4 | 194.4 | 178.8 | 23.5 | 0.83
2936 | 558.3 | 238.9 | 505.7 | 24.8 | 2.22
2937 | 644.4 | 316.7 | 407.2 | 26.8 | 1.67
2938 | 758.3 | 313.9 | 479.2 | 28 | 3.33
2939 | 869.4 | 377.8 | 496.1 | 29.5 | 1.67
2940 | 758.3 | 380.6 | 381.2 | 31.5 | 2.22
2941 | 752.8 | 341.7 | 443.2 | 31.9 | 1.67
2942 | 711.1 | 333.3 | 469.3 | 32 | 1.67
2943 | 408.3 | 322.2 | 136.3 | 32.2 | 2.78
2944 | 352.8 | 191.7 | 384.2 | 32.3 | 2.78
2945 | 77.8 | 61.1 | 91.3 | 28.4 | 2.22
2946 | 2.8 | 0 | 0 | 25.8 | 2.78
2947 | 0 | 0 | 0 | 25.5 | 1.94
2948 | 0 | 0 | 0 | 23.9 | 3.89
2949 | 0 | 0 | 0 | 23.9 | 2.22
2950 | 0 | 0 | 0 | 23.9 | 5.56
2951 | 0 | 0 | 0 | 23.4 | 2.22
2952 | 0 | 0 | 0 | 23.4 | 1.11
2953 | 0 | 0 | 0 | 23.4 | 3.33
2954 | 0 | 0 | 0 | 22.8 | 4.44
2955 | 0 | 0 | 0 | 22.4 | 4.44
2956 | 0 | 0 | 0 | 22 | 3.61
2957 | 19.4 | 0 | 0 | 21.9 | 3.33
2958 | 152.8 | 52.8 | 421.6 | 22 | 3.33
2959 | 283.3 | 152.8 | 310.9 | 22.8 | 2.5
2960 | 483.3 | 258.3 | 356.1 | 24 | 3.89
2961 | 355.6 | 300 | 69 | 25.7 | 2.78
2962 | 680.6 | 325 | 383.4 | 27.4 | 2.78
2963 | 988.9 | 202.8 | 793.5 | 29.3 | 2.78
2964 | 880.6 | 147.2 | 740.2 | 31 | 2.22
2965 | 794.4 | 250 | 587.1 | 32 | 1.67
2966 | 502.8 | 305.6 | 245 | 32.9 | 2.78
2967 | 277.8 | 269.4 | 13.2 | 31.8 | 4.44
2968 | 169.4 | 147.2 | 52.9 | 31.4 | 2.78
2969 | 55.6 | 47.2 | 45.4 | 31 | 2.78
2970 | 0 | 2.8 | 0 | 30.4 | 1.94
2971 | 0 | 0 | 0 | 28.5 | 2.22
2972 | 0 | 0 | 0 | 27.4 | 2.78
2973 | 0 | 0 | 0 | 26.7 | 2.22
2974 | 0 | 0 | 0 | 26.7 | 2.22
2975 | 0 | 0 | 0 | 26 | 3.33
2976 | 0 | 0 | 0 | 25.9 | 1.39
2977 | 0 | 0 | 0 | 24.4 | 4.42
2978 | 0 | 0 | 0 | 23.6 | 4.34
2979 | 0 | 0 | 0 | 23 | 4.06
2980 | 0 | 0 | 0 | 22.5 | 3.71
2981 | 8.3 | 0 | 0 | 22 | 3.64
2982 | 127.8 | 63.9 | 346.3 | 22.5 | 3.36
2983 | 263.9 | 197.2 | 158.5 | 24.2 | 3.66
2984 | 425 | 283.3 | 224.1 | 26 | 4.19
2985 | 750 | 255.6 | 614.2 | 27.5 | 4.17
2986 | 863.9 | 186.1 | 731 | 29 | 4.38
2987 | 850 | 194.4 | 661.9 | 30.8 | 4.34
2988 | 902.8 | 191.7 | 717.9 | 31.9 | 3.89
2989 | 825 | 225 | 647.1 | 32.2 | 3.68
2990 | 597.2 | 244.4 | 438.2 | 32.4 | 3.57
2991 | 566.7 | 200 | 580 | 33.1 | 3.45
2992 | 133.3 | 119.4 | 33 | 32.7 | 3.68
2993 | 69.4 | 36.1 | 180.7 | 24 | 3.34
2994 | 5.6 | 0 | 0 | 25.5 | 3.48
2995 | 0 | 0 | 0 | 26 | 3.18
2996 | 0 | 0 | 0 | 22.7 | 2.94
2997 | 0 | 0 | 0 | 22.5 | 3.66
2998 | 0 | 0 | 0 | 21.9 | 4.16
2999 | 0 | 0 | 0 | 22.5 | 4.69
3000 | 0 | 0 | 0 | 22.9 | 1.67
3001 | 0 | 0 | 0 | 23 | 4.44
3002 | 0 | 0 | 0 | 23.1 | 3.33
3003 | 0 | 0 | 0 | 23.5 | 3.33
3004 | 0 | 0 | 0 | 22.5 | 1.67
3005 | 11.1 | 5.6 | 0 | 21.8 | 3.61
3006 | 205.6 | 122.2 | 425.7 | 22.4 | 3.06
3007 | 405.6 | 144.4 | 620.1 | 24.4 | 3.89
3008 | 580.6 | 175 | 641.2 | 25.8 | 4.44
3009 | 733.3 | 191.7 | 672.9 | 27.4 | 5.56
3010 | 783.3 | 222.2 | 605.3 | 29 | 5
3011 | 863.9 | 213.9 | 656.4 | 30.3 | 5.56
3012 | 872.2 | 400 | 476.9 | 31.6 | 3.33
3013 | 761.1 | 272.2 | 527.4 | 32.6 | 3.33
3014 | 452.8 | 177.8 | 341.6 | 33.7 | 3.89
3015 | 363.9 | 111.1 | 399.7 | 33.9 | 1.67
3016 | 158.3 | 11.1 | 349.6 | 32.8 | 4.44
3017 | 88.9 | 0 | 425.7 | 28 | 3.89
3018 | 2.8 | 0 | 0 | 27.1 | 6.67
3019 | 0 | 0 | 0 | 25.4 | 2.78
3020 | 0 | 0 | 0 | 25.3 | 5.56
3021 | 0 | 0 | 0 | 24.2 | 4.44
3022 | 0 | 0 | 0 | 23.2 | 2.78
3023 | 0 | 0 | 0 | 23.9 | 5.56
3024 | 0 | 0 | 0 | 23.07 | 1.94
3025 | 0 | 0 | 0 | 22.8 | 5.56
3026 | 0 | 0 | 0 | 22.45 | 5.56
3027 | 0 | 0 | 0 | 22.33 | 3.89
3028 | 0 | 0 | 0 | 22.13 | 4.44
3029 | 16.7 | 0 | 0 | 21.92 | 4.44
3030 | 127.8 | 33.3 | 427.6 | 22.18 | 5.56
3031 | 311.1 | 155.6 | 368.9 | 23.34 | 5
3032 | 619.4 | 205.6 | 654.2 | 25.3 | 5
3033 | 722.2 | 216.7 | 628 | 26.85 | 7.22
3034 | 775 | 269.4 | 545.5 | 28.61 | 6.67
3035 | 838.9 | 330.6 | 513.5 | 30.5 | 5.56
3036 | 497.2 | 377.8 | 120.7 | 31.7 | 6.11
3037 | 577.8 | 405.6 | 185.8 | 32.58 | 3.89
3038 | 622.2 | 383.3 | 296.8 | 33.17 | 5
3039 | 377.8 | 258.3 | 188.8 | 32.41 | 5
3040 | 319.4 | 213.9 | 250.3 | 31.82 | 2.78
3041 | 86.1 | 77.8 | 44.7 | 30.47 | 3.33
3042 | 0 | 0 | 0 | 28.72 | 3.61
3043 | 0 | 0 | 0 | 27.63 | 7.78
3044 | 0 | 0 | 0 | 26.34 | 5.28
3045 | 0 | 0 | 0 | 25.32 | 5.56
3046 | 0 | 0 | 0 | 24.49 | 5
3047 | 0 | 0 | 0 | 23.68 | 3.89
3048 | 0 | 0 | 0 | 23.5 | 2.22
3049 | 0 | 0 | 0 | 23.5 | 1.67
3050 | 0 | 0 | 0 | 22.2 | 6.11
3051 | 0 | 0 | 0 | 22.1 | 3.33
3052 | 0 | 0 | 0 | 22 | 5
3053 | 2.8 | 5.6 | 0 | 21.8 | 4.44
3054 | 100 | 86.1 | 74.2 | 22 | 2.22
3055 | 327.8 | 158.3 | 401.4 | 23.4 | 2.78
3056 | 544.4 | 191.7 | 557.4 | 25.5 | 3.89
3057 | 719.4 | 200 | 645.3 | 27.5 | 5
3058 | 850 | 202.8 | 698.5 | 29.1 | 3.33
3059 | 897.2 | 208.3 | 696.1 | 31 | 4.44
3060 | 900 | 227.8 | 679.3 | 31.7 | 3.33
3061 | 836.1 | 238.9 | 644.5 | 32.58 | 3.89
3062 | 711.1 | 230.6 | 597 | 33.17 | 3.89
3063 | 555.6 | 191.7 | 575 | 32.41 | 2.78
3064 | 341.7 | 150 | 454 | 31.82 | 2.78
3065 | 116.7 | 61.1 | 296.9 | 33.5 | 2.22
3066 | 0 | 0 | 0 | 28.72 | 2.78
3067 | 0 | 0 | 0 | 27.63 | 1.67
3068 | 0 | 0 | 0 | 26.34 | 0.56
3069 | 0 | 0 | 0 | 25.32 | 0.83
3070 | 0 | 0 | 0 | 24.49 | 7.22
3071 | 0 | 0 | 0 | 23.68 | 7.78
3072 | 0 | 0 | 0 | 23.6 | 2.5
3073 | 0 | 0 | 0 | 23.3 | 8.89
3074 | 0 | 0 | 0 | 22.7 | 8.33
3075 | 0 | 0 | 0 | 22.4 | 7.78
3076 | 0 | 0 | 0 | 22 | 6.67
3077 | 0 | 2.8 | 0 | 21.6 | 6.11
3078 | 75 | 77.8 | 0 | 22.1 | 3.33
3079 | 158.3 | 150 | 19.7 | 22.8 | 4.44
3080 | 269.4 | 225 | 70.2 | 23.9 | 5
3081 | 625 | 419.4 | 255.4 | 25.3 | 3.89
3082 | 813.9 | 369.4 | 479.8 | 28.2 | 6.11
3083 | 916.7 | 186.1 | 738.5 | 30.3 | 4.44
3084 | 930.6 | 172.2 | 766.6 | 31.8 | 4.44
3085 | 880.6 | 172.2 | 764.6 | 33.2 | 5
3086 | 680.6 | 161.1 | 645.4 | 34.2 | 3.89
3087 | 561.1 | 133.3 | 675.7 | 34 | 5
3088 | 386.1 | 108.3 | 657.2 | 34 | 4.17
3089 | 161.1 | 47.2 | 431.4 | 33.1 | 3.33
3090 | 11.1 | 0 | 0 | 31.9 | 2.78
3091 | 0 | 0 | 0 | 29.9 | 1.39
3092 | 0 | 0 | 0 | 27.7 | 1.67
3093 | 0 | 0 | 0 | 27.8 | 2.78
3094 | 0 | 0 | 0 | 26.6 | 5.56
3095 | 0 | 0 | 0 | 25.5 | 4.44
3096 | 0 | 0 | 0 | 24.7 | 2.78
3097 | 0 | 0 | 0 | 23.4 | 5
3098 | 0 | 0 | 0 | 22.6 | 5.56
3099 | 0 | 0 | 0 | 22.1 | 3.89
3100 | 0 | 0 | 0 | 21.6 | 4.44
3101 | 2.8 | 0 | 0 | 21 | 3.33
3102 | 122.2 | 11.1 | 433.2 | 21.4 | 3.89
3103 | 363.9 | 86.1 | 656.4 | 23.4 | 3.33
3104 | 580.6 | 122.2 | 723.8 | 25.2 | 4.44
3105 | 750 | 150 | 745.5 | 27 | 3.33
3106 | 869.4 | 141.7 | 785.8 | 29.5 | 5
3107 | 922.2 | 141.7 | 789.3 | 31.5 | 5
3108 | 913.9 | 158.3 | 764 | 33.2 | 4.44
3109 | 858.3 | 158.3 | 755.9 | 33.5 | 5.56
3110 | 675 | 141.7 | 662.7 | 33.9 | 5.56
3111 | 586.1 | 127.8 | 723.8 | 34 | 4.44
3112 | 372.2 | 91.7 | 663 | 33.7 | 3.89
3113 | 141.7 | 22.2 | 433.2 | 33.2 | 3.33
3114 | 5.6 | 0 | 0 | 31.4 | 2.78
3115 | 0 | 0 | 0 | 30.7 | 1.11
3116 | 0 | 0 | 0 | 28.8 | 1.67
3117 | 0 | 0 | 0 | 27.6 | 4.44
3118 | 0 | 0 | 0 | 26.3 | 4.44
3119 | 0 | 0 | 0 | 25.7 | 5.56
3120 | 0 | 0 | 0 | 23.07 | 3.06
3121 | 0 | 0 | 0 | 22.8 | 4.44
3122 | 0 | 0 | 0 | 22.45 | 5
3123 | 0 | 0 | 0 | 22.33 | 3.33
3124 | 0 | 0 | 0 | 22.13 | 3.89
3125 | 0 | 0 | 0 | 21.92 | 4.44
3126 | 55.6 | 55.6 | 0 | 22.18 | 3.33
3127 | 277.8 | 205.6 | 170.5 | 23.34 | 2.78
3128 | 566.7 | 261.1 | 482.4 | 25.3 | 2.78
3129 | 711.1 | 275 | 541.9 | 26.85 | 5.56
3130 | 836.1 | 202.8 | 684.1 | 28.61 | 5
3131 | 877.8 | 202.8 | 682.8 | 30.5 | 4.44
3132 | 858.3 | 263.9 | 601.3 | 31.7 | 3.89
3133 | 827.8 | 208.3 | 669.1 | 32.58 | 3.33
3134 | 694.4 | 194.4 | 621.3 | 33.17 | 5
3135 | 388.9 | 183.3 | 324.5 | 32.41 | 3.89
3136 | 169.4 | 122.2 | 111.5 | 31.82 | 2.78
3137 | 91.7 | 66.7 | 131.8 | 30.47 | 3.33
3138 | 5.6 | 0 | 0 | 28.72 | 1.67
3139 | 0 | 0 | 0 | 27.63 | 0.56
3140 | 0 | 0 | 0 | 26.34 | 1.67
3141 | 0 | 0 | 0 | 25.32 | 2.78
3142 | 0 | 0 | 0 | 24.49 | 3.89
3143 | 0 | 0 | 0 | 23.68 | 4.17
3144 | 0 | 0 | 0 | 24 | 3.33
3145 | 0 | 0 | 0 | 23.7 | 1.94
3146 | 0 | 0 | 0 | 23.4 | 3.33
3147 | 0 | 0 | 0 | 22.6 | 2.78
3148 | 0 | 0 | 0 | 22.5 | 2.78
3149 | 5.6 | 13.9 | 0 | 22.3 | 3.33
3150 | 113.9 | 97.2 | 87.5 | 22.3 | 3.89
3151 | 350 | 147.2 | 478.2 | 23.4 | 5.56
3152 | 566.7 | 161.1 | 640.1 | 25 | 4.44
3153 | 727.8 | 169.4 | 693.9 | 26.7 | 4.44
3154 | 841.7 | 177.8 | 717.3 | 28.6 | 3.89
3155 | 891.7 | 177.8 | 722.4 | 30.7 | 3.33
3156 | 897.2 | 175 | 730.9 | 32.1 | 2.78
3157 | 866.7 | 175 | 747.3 | 33.5 | 2.78
3158 | 675 | 244.4 | 535.1 | 34.3 | 3.89
3159 | 394.4 | 247.2 | 232.4 | 33.8 | 2.22
3160 | 341.7 | 211.1 | 307.9 | 33.6 | 1.67
3161 | 105.6 | 83.3 | 116.7 | 32.8 | 1.67
3162 | 5.6 | 2.8 | 0 | 30.5 | 2.78
3163 | 0 | 0 | 0 | 29 | 2.5
3164 | 0 | 0 | 0 | 28 | 1.11
3165 | 0 | 0 | 0 | 26.4 | 3.89
3166 | 0 | 0 | 0 | 25.7 | 5
3167 | 0 | 0 | 0 | 24.1 | 5.56
3168 | 0 | 0 | 0 | 24.4 | 3.61
3169 | 0 | 0 | 0 | 23.9 | 3.89
3170 | 0 | 0 | 0 | 23.2 | 3.06
3171 | 0 | 0 | 0 | 22.6 | 5
3172 | 0 | 0 | 0 | 22.5 | 2.78
3173 | 2.8 | 0 | 0 | 22.3 | 4.44
3174 | 116.7 | 38.9 | 406.8 | 22.3 | 5
3175 | 352.8 | 127.8 | 530 | 23.3 | 4.44
3176 | 555.6 | 152.8 | 635.6 | 26.8 | 5
3177 | 722.2 | 166.7 | 690.6 | 28.4 | 5
3178 | 827.8 | 180.6 | 699.5 | 30.3 | 4.44
3179 | 872.2 | 191.7 | 689 | 32.2 | 6.11
3180 | 880.6 | 202.8 | 686.2 | 33 | 4.44
3181 | 777.8 | 294.4 | 522.4 | 33.9 | 2.78
3182 | 438.9 | 227.8 | 262.4 | 34.3 | 2.78
3183 | 438.9 | 227.8 | 333.1 | 21.4 | 3.89
3184 | 191.7 | 144.4 | 111.2 | 23 | 11.11
3185 | 111.1 | 75 | 188.9 | 23.3 | 8.33
3186 | 0 | 0 | 0 | 23.1 | 5.56
3187 | 0 | 0 | 0 | 22.8 | 3.61
3188 | 0 | 0 | 0 | 23.4 | 2.78
3189 | 0 | 0 | 0 | 24 | 1.94
3190 | 0 | 0 | 0 | 24 | 3.33
3191 | 0 | 0 | 0 | 22.8 | 1.11
3192 | 0 | 0 | 0 | 22.8 | 3.89
3193 | 0 | 0 | 0 | 23.1 | 6.11
3194 | 0 | 0 | 0 | 22.8 | 5.56
3195 | 0 | 0 | 0 | 22.3 | 3.89
3196 | 0 | 0 | 0 | 21.8 | 2.22
3197 | 2.8 | 2.8 | 0 | 21.8 | 2.78
3198 | 75 | 83.3 | 0 | 21.8 | 1.39
3199 | 355.6 | 144.4 | 496.8 | 23.3 | 2.22
3200 | 538.9 | 261.1 | 438.3 | 26.5 | 2.22
3201 | 741.7 | 152.8 | 732.1 | 28 | 3.33
3202 | 780.6 | 266.7 | 555.6 | 29.8 | 2.78
3203 | 852.8 | 208.3 | 652.7 | 31.1 | 2.78
3204 | 858.3 | 152.8 | 714.6 | 32.3 | 2.78
3205 | 772.2 | 169.4 | 651.7 | 33.2 | 2.78
3206 | 705.6 | 175 | 659.6 | 33.7 | 1.67
3207 | 241.7 | 169.4 | 114 | 32.7 | 2.78
3208 | 5.6 | 38.9 | 0 | 32.4 | 2.22
3209 | 16.7 | 25 | 0 | 29.7 | 2.22
3210 | 0 | 0 | 0 | 24.5 | 2.78
3211 | 0 | 0 | 0 | 23.7 | 5.56
3212 | 0 | 0 | 0 | 22.7 | 3.89
3213 | 0 | 0 | 0 | 22.4 | 2.22
3214 | 0 | 0 | 0 | 22.2 | 4.44
3215 | 0 | 0 | 0 | 22.3 | 5
3216 | 0 | 0 | 0 | 22.1 | 4.17
3217 | 0 | 0 | 0 | 22.5 | 1.67
3218 | 0 | 0 | 0 | 22.4 | 4.44
3219 | 0 | 0 | 0 | 21.9 | 5.56
3220 | 0 | 0 | 0 | 21.8 | 5.56
3221 | 11.1 | 2.8 | 0 | 21.7 | 4.44
3222 | 186.1 | 83.3 | 441.4 | 21.7 | 3.61
3223 | 294.4 | 125 | 398.4 | 22.4 | 3.33
3224 | 538.9 | 147.2 | 617.9 | 25.7 | 5.56
3225 | 727.8 | 172.2 | 690.8 | 26.9 | 3.33
3226 | 827.8 | 158.3 | 724 | 28.4 | 2.78
3227 | 861.1 | 177.8 | 692.4 | 29.4 | 3.89
3228 | 852.8 | 227.8 | 633.3 | 30.3 | 2.78
3229 | 811.1 | 247.2 | 609.9 | 31.4 | 3.33
3230 | 666.7 | 205.6 | 573.4 | 32.2 | 1.94
3231 | 469.4 | 219.4 | 394.4 | 31.8 | 2.78
3232 | 202.8 | 144.4 | 137.2 | 26.5 | 6.67
3233 | 122.2 | 94.4 | 144.2 | 24.9 | 5.56
3234 | 11.1 | 5.6 | 0 | 24.7 | 2.78
3235 | 0 | 0 | 0 | 22.9 | 3.33
3236 | 0 | 0 | 0 | 23 | 5
3237 | 0 | 0 | 0 | 22.9 | 3.89
3238 | 0 | 0 | 0 | 22 | 3.89
3239 | 0 | 0 | 0 | 21.7 | 6.67
3240 | 0 | 0 | 0 | 21.7 | 4.44
3241 | 0 | 0 | 0 | 21.5 | 6.94
3242 | 0 | 0 | 0 | 21.4 | 6.11
3243 | 0 | 0 | 0 | 21.4 | 6.11
3244 | 0 | 0 | 0 | 21.5 | 5
3245 | 8.3 | 0 | 0 | 21.2 | 3.89
3246 | 127.8 | 22.2 | 442.9 | 21.3 | 3.33
3247 | 383.3 | 144.4 | 561.2 | 22.7 | 3.33
3248 | 427.8 | 297.2 | 205.9 | 24.1 | 5.56
3249 | 469.4 | 438.9 | 38 | 25 | 3.89
3250 | 463.9 | 411.1 | 57.1 | 26.4 | 5
3251 | 891.7 | 244.4 | 656.1 | 29.5 | 5
3252 | 847.2 | 205.6 | 650.4 | 30.3 | 5.56
3253 | 791.7 | 202.8 | 637.1 | 31.5 | 5.56
3254 | 683.3 | 194.4 | 608 | 32.3 | 4.44
3255 | 519.4 | 172.2 | 547.7 | 32.4 | 5.56
3256 | 325 | 141.7 | 430.7 | 32.5 | 5.56
3257 | 105.6 | 69.4 | 186.7 | 31.2 | 4.44
3258 | 8.3 | 2.8 | 0 | 29.4 | 3.89
3259 | 0 | 0 | 0 | 28.1 | 3.89
3260 | 0 | 0 | 0 | 27.5 | 3.89
3261 | 0 | 0 | 0 | 26.9 | 4.44
3262 | 0 | 0 | 0 | 25 | 7.22
3263 | 0 | 0 | 0 | 24 | 7.78
3264 | 0 | 0 | 0 | 23.1 | 4.72
3265 | 0 | 0 | 0 | 22.7 | 7.78
3266 | 0 | 0 | 0 | 22.4 | 6.67
3267 | 0 | 0 | 0 | 22.5 | 6.11
3268 | 0 | 0 | 0 | 22.3 | 7.22
3269 | 0 | 0 | 0 | 22 | 5.56
3270 | 80.6 | 69.4 | 57.2 | 22 | 5.56
3271 | 313.9 | 144.4 | 397.7 | 22.2 | 6.11
3272 | 547.2 | 183.3 | 573.9 | 25 | 7.22
3273 | 719.4 | 197.2 | 649.6 | 26.5 | 4.44
3274 | 836.1 | 202.8 | 685.5 | 28.6 | 5
3275 | 861.1 | 205.6 | 664.8 | 30 | 5.56
3276 | 872.2 | 202.8 | 678.9 | 31.5 | 5
3277 | 822.2 | 197.2 | 676.5 | 32.7 | 5
3278 | 708.3 | 177.8 | 660 | 33.3 | 5
3279 | 561.1 | 158.3 | 635.2 | 33.3 | 2.78
3280 | 366.7 | 116.7 | 586.8 | 33.2 | 2.78
3281 | 158.3 | 47.2 | 444.3 | 32.9 | 2.78
3282 | 8.3 | 0 | 0 | 31.7 | 2.78
3283 | 0 | 0 | 0 | 30.5 | 1.67
3284 | 0 | 0 | 0 | 28.5 | 1.11
3285 | 0 | 0 | 0 | 27.8 | 2.22
3286 | 0 | 0 | 0 | 26.5 | 4.44
3287 | 0 | 0 | 0 | 25.5 | 5.56
3288 | 0 | 0 | 0 | 24.3 | 5
3289 | 0 | 0 | 0 | 23.5 | 5.56
3290 | 0 | 0 | 0 | 22.9 | 6.67
3291 | 0 | 0 | 0 | 22.3 | 6.11
3292 | 0 | 0 | 0 | 21.8 | 5
3293 | 22.2 | 0 | 0 | 21.5 | 4.44
3294 | 213.9 | 50 | 445.7 | 21.6 | 5.56
3295 | 433.3 | 119.4 | 730.3 | 21.9 | 7.22
3296 | 625 | 158.3 | 735.9 | 24.4 | 6.11
3297 | 777.8 | 163.9 | 763.8 | 25 | 4.44
3298 | 875 | 177.8 | 754.9 | 26.5 | 5.56
3299 | 908.3 | 183.3 | 735.5 | 30.9 | 5.56
3300 | 886.1 | 163.9 | 732.7 | 32 | 3.33
3301 | 811.1 | 161.1 | 703.8 | 33.4 | 4.44
3302 | 669.4 | 152.8 | 642.9 | 34.1 | 4.17
3303 | 475 | 122.2 | 556.3 | 34.3 | 4.44
3304 | 222.2 | 97.2 | 293.1 | 34.3 | 3.89
3305 | 30.6 | 41.7 | 0 | 34 | 2.78
3306 | 0 | 0 | 0 | 31.9 | 4.17
3307 | 0 | 0 | 0 | 30 | 2.22
3308 | 0 | 0 | 0 | 29.2 | 3.89
3309 | 0 | 0 | 0 | 27.9 | 5
3310 | 0 | 0 | 0 | 26.5 | 5.56
3311 | 0 | 0 | 0 | 25.3 | 7.78
3312 | 0 | 0 | 0 | 24.3 | 5.28
3313 | 0 | 0 | 0 | 23.5 | 6.67
3314 | 0 | 0 | 0 | 22.5 | 5
3315 | 0 | 0 | 0 | 22 | 5
3316 | 0 | 0 | 0 | 21.6 | 6.67
3317 | 2.8 | 16.7 | 0 | 21.5 | 6.11
3318 | 144.4 | 97.2 | 241.6 | 21.5 | 5.56
3319 | 369.4 | 125 | 572.8 | 23.1 | 5.56
3320 | 597.2 | 161.1 | 687.7 | 24 | 6.67
3321 | 738.9 | 166.7 | 712.2 | 25.3 | 6.11
3322 | 852.8 | 194.4 | 713.1 | 26.7 | 6.11
3323 | 877.8 | 225 | 662.6 | 29.9 | 6.11
3324 | 911.1 | 208.3 | 713.3 | 31.2 | 5.56
3325 | 858.3 | 205.6 | 707 | 32.5 | 5.56
3326 | 683.3 | 283.3 | 497.8 | 33.2 | 6.11
3327 | 450 | 297.2 | 240.9 | 33.1 | 5.56
3328 | 313.9 | 194.4 | 279.9 | 32.9 | 5.56
3329 | 119.4 | 113.9 | 28.4 | 31.4 | 6.67
3330 | 5.6 | 8.3 | 0 | 29.9 | 6.67
3331 | 0 | 0 | 0 | 28.7 | 6.11
3332 | 0 | 0 | 0 | 27.4 | 5.56
3333 | 0 | 0 | 0 | 26 | 6.67
3334 | 0 | 0 | 0 | 24.8 | 6.67
3335 | 0 | 0 | 0 | 23.9 | 7.22
3336 | 0 | 0 | 0 | 23.07 | 5.56
3337 | 0 | 0 | 0 | 22.8 | 5.56
3338 | 0 | 0 | 0 | 22.45 | 5.56
3339 | 0 | 0 | 0 | 22.33 | 5.56
3340 | 0 | 0 | 0 | 22.13 | 4.44
3341 | 5.6 | 19.4 | 0 | 21.92 | 5
3342 | 138.9 | 94.4 | 226.7 | 22.18 | 5.56
3343 | 372.2 | 147.2 | 526.8 | 23.34 | 5.56
3344 | 569.4 | 191.7 | 595.7 | 25.3 | 6.11
3345 | 722.2 | 202.8 | 646.6 | 26.85 | 5
3346 | 852.8 | 227.8 | 677.2 | 28.61 | 5.56
3347 | 883.3 | 261.1 | 631.8 | 30.5 | 6.11
3348 | 866.7 | 311.1 | 564.1 | 31.7 | 3.89
3349 | 738.9 | 344.4 | 427.4 | 32.58 | 3.89
3350 | 697.2 | 294.4 | 501.4 | 33.17 | 4.44
3351 | 488.9 | 225 | 416.1 | 32.41 | 2.78
3352 | 397.2 | 141.7 | 598.4 | 31.82 | 2.78
3353 | 152.8 | 83.3 | 354.2 | 30.47 | 2.22
3354 | 5.6 | 8.3 | 0 | 30.4 | 2.78
3355 | 0 | 0 | 0 | 29.4 | 3.89
3356 | 0 | 0 | 0 | 28.6 | 4.44
3357 | 0 | 0 | 0 | 27.4 | 3.89
3358 | 0 | 0 | 0 | 26 | 5.56
3359 | 0 | 0 | 0 | 24.9 | 5
3360 | 0 | 0 | 0 | 24.1 | 5.83
3361 | 0 | 0 | 0 | 23.4 | 3.89
3362 | 0 | 0 | 0 | 22.8 | 3.89
3363 | 0 | 0 | 0 | 22.4 | 4.44
3364 | 0 | 0 | 0 | 22 | 2.78
3365 | 8.3 | 5.6 | 0 | 21.6 | 3.33
3366 | 138.9 | 94.4 | 226 | 22.1 | 2.78
3367 | 375 | 141.7 | 546 | 23.6 | 4.44
3368 | 588.9 | 158.3 | 678.9 | 25.6 | 5
3369 | 744.4 | 163.9 | 722.9 | 27.2 | 4.44
3370 | 847.2 | 163.9 | 740.7 | 28.7 | 6.67
3371 | 894.4 | 175 | 730.9 | 30.8 | 5.56
3372 | 861.1 | 186.1 | 685.7 | 31.8 | 5.56
3373 | 825 | 208.3 | 668.5 | 32.7 | 5
3374 | 658.3 | 233.3 | 529.2 | 33.1 | 5.56
3375 | 577.8 | 191.7 | 608.8 | 33.1 | 4.44
3376 | 375 | 150 | 526.5 | 32.8 | 5.56
3377 | 94.4 | 77.8 | 84.7 | 31.6 | 4.44
3378 | 8.3 | 8.3 | 0 | 30 | 3.89
3379 | 0 | 0 | 0 | 29.4 | 3.33
3380 | 0 | 0 | 0 | 28.4 | 4.44
3381 | 0 | 0 | 0 | 27.3 | 5.56
3382 | 0 | 0 | 0 | 25.2 | 5.56
3383 | 0 | 0 | 0 | 24.8 | 4.44
3384 | 0 | 0 | 0 | 24.6 | 6.11
3385 | 0 | 0 | 0 | 24.6 | 2.78
3386 | 0 | 0 | 0 | 24.2 | 2.78
3387 | 0 | 0 | 0 | 24.1 | 1.11
3388 | 0 | 0 | 0 | 24 | 1.39
3389 | 0 | 0 | 0 | 23.7 | 1.94
3390 | 50 | 33.3 | 84.5 | 23.7 | 1.67
3391 | 277.8 | 138.9 | 324.8 | 25.2 | 2.78
3392 | 561.1 | 172.2 | 613.2 | 27 | 3.89
3393 | 758.3 | 180.6 | 719.6 | 28.5 | 3.33
3394 | 866.7 | 180.6 | 744 | 30.2 | 4.44
3395 | 848.3 | 257.1 | 599.2 | 31.3 | 3.89
3396 | 838 | 263.8 | 582 | 32.2 | 5.56
3397 | 779.2 | 266.9 | 550.3 | 32.9 | 2.22
3398 | 769.4 | 200 | 709.2 | 34 | 3.33
3399 | 588.9 | 177.8 | 648.2 | 34 | 1.67
3400 | 344.4 | 113.9 | 539.1 | 33.8 | 2.78
3401 | 100 | 47.2 | 267.6 | 33.2 | 3.89
3402 | 0 | 0 | 0 | 31.5 | 2.78
3403 | 0 | 0 | 0 | 30 | 2.78
3404 | 0 | 0 | 0 | 26.7 | 1.11
3405 | 0 | 0 | 0 | 26 | 3.89
3406 | 0 | 0 | 0 | 24.4 | 1.94
3407 | 0 | 0 | 0 | 22.9 | 5
3408 | 0 | 0 | 0 | 22.5 | 6.39
3409 | 0 | 0 | 0 | 21.9 | 3.89
3410 | 0 | 0 | 0 | 22 | 2.78
3411 | 0 | 0 | 0 | 23 | 1.39
3412 | 0 | 0 | 0 | 23.1 | 1.11
3413 | 0 | 0 | 0 | 23.1 | 2.5
3414 | 97.2 | 36.1 | 308.9 | 23.6 | 2.78
3415 | 344.4 | 113.9 | 538.8 | 25.4 | 2.78
3416 | 461.1 | 233.3 | 359.1 | 27.1 | 4.44
3417 | 733.3 | 233.3 | 622.9 | 28.8 | 5.56
3418 | 838.9 | 202.8 | 690.1 | 30.5 | 4.44
3419 | 883.3 | 216.7 | 677.9 | 32 | 5
3420 | 872.2 | 263.9 | 618.6 | 33.3 | 2.78
3421 | 588.9 | 355.6 | 253.1 | 33.5 | 1.67
3422 | 430.6 | 261.1 | 211.1 | 34.4 | 1.67
3423 | 186.1 | 163.9 | 35 | 33.3 | 2.78
3424 | 127.8 | 113.9 | 32.5 | 31.3 | 1.11
3425 | 86.1 | 47.2 | 196.6 | 29.7 | 3.89
3426 | 0 | 0 | 0 | 26.2 | 3.33
3427 | 0 | 0 | 0 | 25.7 | 4.44
3428 | 0 | 0 | 0 | 26.3 | 3.33
3429 | 0 | 0 | 0 | 23.5 | 6.67
3430 | 0 | 0 | 0 | 24 | 5.56
3431 | 0 | 0 | 0 | 23.1 | 5
3432 | 0 | 0 | 0 | 22.8 | 6.67
3433 | 0 | 0 | 0 | 22.3 | 3.33
3434 | 0 | 0 | 0 | 22.1 | 3.33
3435 | 0 | 0 | 0 | 22 | 3.33
3436 | 0 | 0 | 0 | 21.5 | 2.78
3437 | 5.6 | 11.1 | 0 | 21.3 | 4.44
3438 | 125 | 88.9 | 182 | 21.5 | 4.44
3439 | 363.9 | 158.3 | 480 | 23.6 | 4.44
3440 | 569.4 | 188.9 | 600 | 26 | 3.89
3441 | 727.8 | 200 | 657.7 | 27.5 | 5.56
3442 | 836.1 | 227.8 | 660.2 | 29 | 5
3443 | 891.7 | 233.3 | 669.7 | 31.3 | 3.89
3444 | 880.6 | 252.8 | 638.6 | 31.7 | 3.89
3445 | 841.7 | 261.1 | 630 | 32.7 | 4.17
3446 | 619.4 | 286.1 | 415.4 | 33.5 | 2.22
3447 | 455.6 | 252.8 | 319.7 | 33.3 | 2.78
3448 | 361.1 | 197.2 | 382.7 | 33 | 2.78
3449 | 116.7 | 47.2 | 350 | 33 | 3.33
3450 | 2.8 | 0 | 0 | 31 | 3.89
3451 | 0 | 0 | 0 | 29.7 | 3.33
3452 | 0 | 0 | 0 | 29.1 | 3.89
3453 | 0 | 0 | 0 | 23 | 4.44
3454 | 0 | 0 | 0 | 23.4 | 1.11
3455 | 0 | 0 | 0 | 22.9 | 5.56
3456 | 0 | 0 | 0 | 17.4 | 6.94
3457 | 0 | 0 | 0 | 18.3 | 6.67
3458 | 0 | 0 | 0 | 20.1 | 2.78
3459 | 0 | 0 | 0 | 21.1 | 3.33
3460 | 0 | 0 | 0 | 21.5 | 3.89
3461 | 5.7 | 0 | 0 | 21.5 | 2.78
3462 | 113.7 | 105.6 | 265 | 22 | 3.33
3463 | 312.7 | 188.9 | 396.5 | 23.5 | 2.78
3464 | 519.6 | 211.1 | 476.9 | 24.8 | 2.78
3465 | 675.9 | 250 | 530.2 | 26.4 | 4.44
3466 | 794.7 | 272.2 | 575.5 | 28.2 | 4.44
3467 | 877.8 | 266.7 | 621.9 | 30.1 | 4.44
3468 | 880.6 | 269.4 | 621.9 | 31.2 | 3.33
3469 | 827.8 | 269.4 | 606.2 | 32.4 | 3.89
3470 | 730.6 | 258.3 | 588.6 | 33.2 | 3.33
3471 | 300 | 180.6 | 188.3 | 33.8 | 2.78
3472 | 227.8 | 141.7 | 201 | 31.6 | 2.22
3473 | 144.4 | 66.7 | 391 | 30.3 | 2.22
3474 | 8.3 | 0 | 0 | 27.8 | 2.78
3475 | 0 | 0 | 0 | 26.8 | 1.94
3476 | 0 | 0 | 0 | 26.5 | 1.67
3477 | 0 | 0 | 0 | 25.7 | 3.89
3478 | 0 | 0 | 0 | 24.2 | 5
3479 | 0 | 0 | 0 | 23.3 | 6.11
3480 | 0 | 0 | 0 | 22.6 | 7.22
3481 | 0 | 0 | 0 | 22 | 5
3482 | 0 | 0 | 0 | 21.8 | 3.89
3483 | 0 | 0 | 0 | 21.5 | 4.44
3484 | 0 | 0 | 0 | 21.5 | 3.89
3485 | 8.3 | 0 | 0 | 21.3 | 3.89
3486 | 122.2 | 72.2 | 250.7 | 21.3 | 2.78
3487 | 341.7 | 163.9 | 414.7 | 22.7 | 3.61
3488 | 555.6 | 205.6 | 551.8 | 24.4 | 5
3489 | 719.4 | 244.4 | 592.2 | 26 | 5
3490 | 825 | 261.1 | 612.4 | 28.5 | 4.72
3491 | 848.3 | 257.1 | 599.2 | 30.3 | 4.44
3492 | 838 | 263.8 | 582 | 32 | 4.44
3493 | 888.9 | 266.9 | 550.3 | 32.7 | 3.89
3494 | 727.8 | 258.3 | 585.3 | 33.9 | 4.17
3495 | 555.6 | 219.4 | 529.9 | 33.8 | 3.33
3496 | 316.7 | 130.6 | 434.1 | 33.9 | 2.22
3497 | 138.9 | 55.6 | 417.9 | 33.5 | 2.78
3498 | 8.3 | 0 | 0 | 32.4 | 2.22
3499 | 0 | 0 | 0 | 31 | 1.67
3500 | 0 | 0 | 0 | 27.8 | 1.11
3501 | 0 | 0 | 0 | 26 | 6.11
3502 | 0 | 0 | 0 | 25.3 | 6.67
3503 | 0 | 0 | 0 | 24.7 | 5.56
3504 | 0 | 0 | 0 | 24.4 | 7.5
3505 | 0 | 0 | 0 | 24.2 | 4.44
3506 | 0 | 0 | 0 | 22.5 | 4.44
3507 | 0 | 0 | 0 | 22.5 | 4.44
3508 | 0 | 0 | 0 | 22.5 | 3.89
3509 | 0 | 11.1 | 0 | 22.5 | 4.44
3510 | 94.4 | 122.2 | 0 | 23 | 3.89
3511 | 283.3 | 216.7 | 155.4 | 23.5 | 3.89
3512 | 558.3 | 252.8 | 481.8 | 25.6 | 3.33
3513 | 577.8 | 305.6 | 339.5 | 26.8 | 2.78
3514 | 847.2 | 216.7 | 685.1 | 29.5 | 2.78
3515 | 875 | 200 | 687.5 | 31.2 | 5
3516 | 872.2 | 200 | 684.7 | 32.7 | 3.33
3517 | 822.2 | 200 | 676 | 33.7 | 3.33
3518 | 722.2 | 227.8 | 616.6 | 34 | 2.22
3519 | 430.6 | 222.2 | 328.5 | 34.1 | 2.78
3520 | 213.9 | 150 | 149 | 34.4 | 3.33
3521 | 105.6 | 88.9 | 83.4 | 33.9 | 2.22
3522 | 8.3 | 19.4 | 0 | 33.3 | 3.33
3523 | 0 | 0 | 0 | 32.3 | 2.78
3524 | 0 | 0 | 0 | 27.8 | 1.11
3525 | 0 | 0 | 0 | 27.1 | 2.5
3526 | 0 | 0 | 0 | 26.8 | 2.78
3527 | 0 | 0 | 0 | 25.1 | 5
3528 | 0 | 0 | 0 | 24.3 | 7.78
3529 | 0 | 0 | 0 | 24 | 6.67
3530 | 0 | 0 | 0 | 23.3 | 6.67
3531 | 0 | 0 | 0 | 23 | 7.22
3532 | 0 | 0 | 0 | 22.9 | 6.67
3533 | 0 | 0 | 0 | 22.6 | 5.56
3534 | 52.8 | 63.9 | 0 | 22.8 | 5
3535 | 141.7 | 152.8 | 0 | 23 | 4.44
3536 | 288.9 | 277.8 | 17.5 | 24.4 | 2.78
3537 | 705.6 | 286.1 | 523.2 | 26.6 | 4.44
3538 | 836.1 | 211.1 | 679.3 | 29.2 | 3.33
3539 | 872.2 | 200 | 685 | 30.7 | 5
3540 | 900 | 188.9 | 724.6 | 32.2 | 3.89
3541 | 847.2 | 194.4 | 709.5 | 32.6 | 4.44
3542 | 738.9 | 175 | 703.4 | 33.4 | 2.22
3543 | 572.2 | 158.3 | 652.6 | 33.5 | 3.33
3544 | 377.8 | 141.7 | 550.2 | 33.4 | 2.22
3545 | 152.8 | 88.9 | 318.8 | 32.7 | 2.22
3546 | 8.3 | 11.1 | 0 | 32 | 2.78
3547 | 0 | 0 | 0 | 30.7 | 1.67
3548 | 0 | 0 | 0 | 29.4 | 0.56
3549 | 0 | 0 | 0 | 27 | 0.56
3550 | 0 | 0 | 0 | 26 | 0
3551 | 0 | 0 | 0 | 25.1 | 5.56
3552 | 0 | 0 | 0 | 23.07 | 8.06
3553 | 0 | 0 | 0 | 22.8 | 5
3554 | 0 | 0 | 0 | 22.45 | 6.11
3555 | 0 | 0 | 0 | 22.33 | 4.44
3556 | 0 | 0 | 0 | 22.13 | 2.78
3557 | 0 | 0 | 0 | 21.92 | 1.67
3558 | 125 | 77.8 | 235.1 | 22.18 | 1.11
3559 | 330.6 | 136.1 | 452.9 | 23.34 | 2.78
3560 | 425 | 252.8 | 271.6 | 25.3 | 2.78
3561 | 630.6 | 352.8 | 346.6 | 26.85 | 2.22
3562 | 830.6 | 238.9 | 643.3 | 28.61 | 5.56
3563 | 888.9 | 255.6 | 645.6 | 30.5 | 4.44
3564 | 888.9 | 277.8 | 623 | 31.7 | 5
3565 | 805.6 | 283.3 | 567.8 | 32.58 | 4.44
3566 | 738.9 | 275 | 578.8 | 33.17 | 5
3567 | 558.3 | 244.4 | 495 | 32.41 | 3.89
3568 | 325 | 200 | 291.2 | 31.82 | 4.44
3569 | 141.7 | 102.8 | 193.6 | 30.47 | 3.33
3570 | 11.1 | 2.8 | 0 | 30.8 | 3.33
3571 | 0 | 0 | 0 | 30 | 1.39
3572 | 0 | 0 | 0 | 26.7 | 0.56
3573 | 0 | 0 | 0 | 25.8 | 4.44
3574 | 0 | 0 | 0 | 25.1 | 3.33
3575 | 0 | 0 | 0 | 20.4 | 2.22
3576 | 0 | 0 | 0 | 19.4 | 8.33
3577 | 0 | 0 | 0 | 20 | 3.33
3578 | 0 | 0 | 0 | 19.8 | 2.78
3579 | 0 | 0 | 0 | 19.9 | 3.33
3580 | 0 | 0 | 0 | 20.2 | 2.22
3581 | 5.6 | 0 | 0 | 20.3 | 1.39
3582 | 75 | 50 | 124.2 | 20.8 | 2.78
3583 | 286.1 | 191.7 | 219.9 | 21.3 | 2.22
3584 | 547.2 | 294.4 | 398.6 | 25.2 | 2.78
3585 | 611.1 | 344.4 | 332.8 | 27.3 | 4.44
3586 | 663.9 | 525 | 151.1 | 28.61 | 4.44
3587 | 705.6 | 583.3 | 124.6 | 31.2 | 3.89
3588 | 655.6 | 555.6 | 102 | 32.9 | 5
3589 | 788.9 | 516.7 | 296.1 | 33 | 3.89
3590 | 361.1 | 363.9 | 0 | 32.8 | 3.33
3591 | 447.2 | 200 | 389.8 | 31.6 | 3.33
3592 | 252.8 | 155.6 | 226.4 | 30.7 | 3.89
3593 | 100 | 86.1 | 69 | 28.7 | 3.33
3594 | 11.1 | 0 | 0 | 27.5 | 5
3595 | 0 | 0 | 0 | 26.7 | 5
3596 | 0 | 0 | 0 | 24 | 3.33
3597 | 0 | 0 | 0 | 23.1 | 3.89
3598 | 0 | 0 | 0 | 21.6 | 3.89
3599 | 0 | 0 | 0 | 21.5 | 2.22
3600 | 0 | 0 | 0 | 21.8 | 8.61
3601 | 0 | 0 | 0 | 22 | 2.5
3602 | 0 | 0 | 0 | 22.2 | 3.33
3603 | 0 | 0 | 0 | 22.3 | 5
3604 | 0 | 0 | 0 | 22.5 | 3.89
3605 | 0 | 0 | 0 | 22.4 | 3.89
3606 | 41.7 | 30.6 | 55.1 | 22.7 | 2.78
3607 | 69.4 | 61.1 | 19.4 | 23.5 | 4.44
3608 | 419.4 | 283.3 | 214.6 | 24.4 | 4.44
3609 | 569.4 | 369.4 | 249.7 | 26.4 | 3.33
3610 | 683.3 | 558.3 | 136 | 28.4 | 2.78
3611 | 458.3 | 444.4 | 14.2 | 29 | 3.33
3612 | 505.6 | 427.8 | 79.4 | 29.4 | 5.56
3613 | 536.1 | 383.3 | 166.2 | 30.3 | 6.11
3614 | 569.4 | 250 | 398.8 | 30.9 | 2.78
3615 | 619.4 | 266.7 | 556.3 | 27.8 | 3.61
3616 | 144.4 | 138.9 | 12.9 | 25.4 | 5.56
3617 | 8.3 | 5.6 | 13.8 | 24.9 | 3.33
3618 | 0 | 0 | 0 | 22.7 | 6.67
3619 | 0 | 0 | 0 | 20.9 | 3.89
3620 | 0 | 0 | 0 | 20.5 | 6.67
3621 | 0 | 0 | 0 | 20.5 | 3.89
3622 | 0 | 0 | 0 | 20.7 | 2.78
3623 | 0 | 0 | 0 | 20.9 | 1.11
3624 | 0 | 0 | 0 | 20.9 | 0.28
3625 | 0 | 0 | 0 | 20.9 | 0
3626 | 0 | 0 | 0 | 20.9 | 0
3627 | 0 | 0 | 0 | 20.9 | 0
3628 | 0 | 0 | 0 | 20.8 | 3.06
3629 | 2.8 | 0 | 0 | 20.4 | 2.78
3630 | 61.1 | 61.1 | 0 | 20.4 | 2.78
3631 | 238.9 | 191.7 | 109.9 | 20.9 | 0
3632 | 536.1 | 197.2 | 534.5 | 23.1 | 2.22
3633 | 377.8 | 291.7 | 107.5 | 23.6 | 2.5
3634 | 533.3 | 377.8 | 169.3 | 25.2 | 0.56
3635 | 850 | 352.8 | 507.5 | 26.6 | 2.22
3636 | 797.2 | 250 | 558.5 | 27.9 | 3.89
3637 | 772.2 | 258.3 | 559.3 | 28.9 | 3.89
3638 | 647.2 | 225 | 527.2 | 29.7 | 3.89
3639 | 277.8 | 180.6 | 153.3 | 30 | 4.44
3640 | 172.2 | 80.6 | 213.2 | 29.3 | 3.33
3641 | 83.3 | 47.2 | 178.7 | 28.7 | 3.89
3642 | 2.8 | 0 | 0 | 27 | 3.33
3643 | 0 | 0 | 0 | 25.7 | 3.06
3644 | 0 | 0 | 0 | 25.3 | 3.06
3645 | 0 | 0 | 0 | 25 | 1.67
3646 | 0 | 0 | 0 | 24.7 | 1.67
3647 | 0 | 0 | 0 | 24.2 | 1.11
3648 | 0 | 0 | 0 | 23.5 | 0.56
3649 | 0 | 0 | 0 | 23.1 | 6.11
3650 | 0 | 0 | 0 | 22.5 | 3.89
3651 | 0 | 0 | 0 | 22.2 | 3.06
3652 | 0 | 0 | 0 | 22 | 3.89
3653 | 8.3 | 2.8 | 0 | 21.8 | 2.78
3654 | 180.6 | 44.4 | 437.9 | 22.5 | 3.06
3655 | 394.4 | 77.8 | 710.2 | 24 | 2.78
3656 | 583.3 | 100 | 762.3 | 24.7 | 3.89
3657 | 738.9 | 105.6 | 791 | 25.7 | 5
3658 | 855.6 | 113.9 | 807.5 | 27.2 | 4.44
3659 | 841.7 | 180.6 | 675 | 27.7 | 3.33
3660 | 908.3 | 150 | 774.3 | 29.2 | 3.33
3661 | 850 | 172.2 | 738 | 30.6 | 2.78
3662 | 711.1 | 155.6 | 693.9 | 30.5 | 3.33
3663 | 600 | 86.1 | 810.5 | 30.8 | 2.78
3664 | 391.7 | 69.4 | 710.2 | 30.7 | 3.89
3665 | 161.1 | 38.9 | 437.9 | 30.5 | 3.33
3666 | 5.6 | 0 | 0 | 28.7 | 3.61
3667 | 0 | 0 | 0 | 27.7 | 3.33
3668 | 0 | 0 | 0 | 26.7 | 2.22
3669 | 0 | 0 | 0 | 26 | 3.33
3670 | 0 | 0 | 0 | 25.9 | 3.06
3671 | 0 | 0 | 0 | 25.2 | 5.56
3672 | 0 | 0 | 0 | 21.47 | 0.83
3673 | 0 | 0 | 0 | 21.18 | 6.11
3674 | 0 | 0 | 0 | 20.95 | 5
3675 | 0 | 0 | 0 | 20.72 | 4.44
3676 | 0 | 0 | 0 | 20.61 | 4.72
3677 | 13.9 | 2.8 | 0 | 20.39 | 3.89
3678 | 119.4 | 72.2 | 232.8 | 20.63 | 1.94
3679 | 411.1 | 197.2 | 497.2 | 21.68 | 2.78
3680 | 397.2 | 280.6 | 184 | 22.95 | 6.39
3681 | 511.1 | 405.6 | 131.9 | 24.06 | 7.5
3682 | 450 | 425 | 27.2 | 25.38 | 6.11
3683 | 369.4 | 361.1 | 8.5 | 26.45 | 5
3684 | 469.4 | 444.4 | 25.5 | 27.54 | 5
3685 | 505.6 | 486.1 | 21.2 | 27.89 | 6.11
3686 | 386.1 | 388.9 | 0 | 28.09 | 3.89
3687 | 350 | 316.7 | 52.6 | 27.68 | 4.44
3688 | 255.6 | 175 | 187.3 | 27.38 | 3.89
3689 | 61.1 | 55.6 | 27.4 | 26.04 | 5.56
3690 | 0 | 0 | 0 | 23.9 | 5
3691 | 0 | 0 | 0 | 23.3 | 6.67
3692 | 0 | 0 | 0 | 23.6 | 5
3693 | 0 | 0 | 0 | 23.8 | 5
3694 | 0 | 0 | 0 | 23.6 | 5.56
3695 | 0 | 0 | 0 | 23.2 | 4.44
3696 | 0 | 0 | 0 | 23.1 | 1.11
3697 | 0 | 0 | 0 | 23.1 | 3.89
3698 | 0 | 0 | 0 | 23 | 4.17
3699 | 0 | 0 | 0 | 22.4 | 4.72
3700 | 0 | 0 | 0 | 22.2 | 3.33
3701 | 8.3 | 0 | 0 | 21.7 | 3.89
3702 | 86.1 | 41.7 | 218.8 | 22 | 4.17
3703 | 216.7 | 166.7 | 116.2 | 23 | 2.78
3704 | 455.6 | 336.1 | 188.4 | 22.95 | 4.44
3705 | 738.9 | 219.4 | 649.1 | 24.06 | 5
3706 | 813.9 | 127.8 | 747.5 | 25.38 | 5
3707 | 794.4 | 388.9 | 414.4 | 26.45 | 5.56
3708 | 786.1 | 580.6 | 210 | 27.54 | 5
3709 | 586.1 | 563.9 | 24.2 | 27.89 | 4.44
3710 | 672.2 | 294.4 | 472.1 | 28.09 | 4.17
3711 | 91.7 | 100 | 0 | 27.68 | 4.44
3712 | 55.6 | 66.7 | 0 | 27.38 | 3.89
3713 | 22.2 | 22.2 | 0 | 26.04 | 5.56
3714 | 0 | 0 | 0 | 24.98 | 4.44
3715 | 0 | 0 | 0 | 23.88 | 3.33
3716 | 0 | 0 | 0 | 23.05 | 6.39
3717 | 0 | 0 | 0 | 22.55 | 3.33
3718 | 0 | 0 | 0 | 22.27 | 2.78
3719 | 0 | 0 | 0 | 21.73 | 2.78
3720 | 0 | 0 | 0 | 21.47 | 1.39
3721 | 0 | 0 | 0 | 21.18 | 4.44
3722 | 0 | 0 | 0 | 20.95 | 3.89
3723 | 0 | 0 | 0 | 20.72 | 2.78
3724 | 0 | 0 | 0 | 20.61 | 3.33
3725 | 16.7 | 0 | 0 | 20.39 | 3.06
3726 | 97.2 | 80.6 | 81.9 | 20.63 | 3.89
3727 | 147.2 | 141.7 | 12.9 | 21.68 | 3.33
3728 | 227.8 | 222.2 | 8.8 | 22.95 | 3.06
3729 | 358.3 | 352.8 | 6.9 | 24.06 | 3.33
3730 | 416.7 | 444.4 | 0 | 25.38 | 4.44
3731 | 525 | 541.7 | 0 | 26.45 | 4.17
3732 | 622.2 | 463.9 | 161.8 | 27.54 | 2.78
3733 | 483.3 | 502.8 | 0 | 27.89 | 3.89
3734 | 680.6 | 477.8 | 253.4 | 28.09 | 3.33
3735 | 363.9 | 336.1 | 43.8 | 27.68 | 3.33
3736 | 213.9 | 213.9 | 0 | 27.38 | 2.22
3737 | 63.9 | 72.2 | 0 | 26.04 | 3.06
3738 | 0 | 0 | 0 | 28.1 | 2.22
3739 | 0 | 0 | 0 | 27.5 | 1.67
3740 | 0 | 0 | 0 | 21.8 | 1.67
3741 | 0 | 0 | 0 | 20.5 | 3.89
3742 | 0 | 0 | 0 | 23.1 | 3.89
3743 | 0 | 0 | 0 | 21.1 | 3.89
3744 | 0 | 0 | 0 | 21.1 | 1.67
3745 | 0 | 0 | 0 | 20.8 | 4.44
3746 | 0 | 0 | 0 | 20.9 | 4.44
3747 | 0 | 0 | 0 | 21 | 5.83
3748 | 0 | 0 | 0 | 21.1 | 5.56
3749 | 11.1 | 0 | 0 | 21.1 | 6.67
3750 | 166.7 | 27.8 | 440.5 | 21.7 | 5
3751 | 416.7 | 122.2 | 683.9 | 23.9 | 3.06
3752 | 569.4 | 158.3 | 648.5 | 25.8 | 3.89
3753 | 744.4 | 244.4 | 625.1 | 27.4 | 3.33
3754 | 567.4 | 386.1 | 240.5 | 28.8 | 3.33
3755 | 830.6 | 211.1 | 633.3 | 29.3 | 3.89
3756 | 877.8 | 180.6 | 712.9 | 29.8 | 4.44
3757 | 833.3 | 197.2 | 693.5 | 30.3 | 3.89
3758 | 722.2 | 147.2 | 718.8 | 31 | 4.44
3759 | 356.7 | 240.8 | 230 | 31.6 | 3.89
3760 | 207.4 | 153 | 160.6 | 30 | 4.44
3761 | 71.3 | 63.6 | 84.8 | 26.6 | 3.89
3762 | 3 | 4.8 | 0 | 26.3 | 1.67
3763 | 0 | 0 | 0 | 26.7 | 2.5
3764 | 0 | 0 | 0 | 26.3 | 1.11
3765 | 0 | 0 | 0 | 22.2 | 2.78
3766 | 0 | 0 | 0 | 18.5 | 5.56
3767 | 0 | 0 | 0 | 19.4 | 3.89
3768 | 0 | 0 | 0 | 21.47 | 1.94
3769 | 0 | 0 | 0 | 21.18 | 0
3770 | 0 | 0 | 0 | 20.95 | 1.11
3771 | 0 | 0 | 0 | 20.72 | 5.28
3772 | 0 | 0 | 0 | 20.61 | 1.67
3773 | 0 | 0 | 0 | 20.39 | 3.33
3774 | 75 | 52.8 | 108.9 | 20.63 | 3.89
3775 | 163.9 | 166.7 | 0 | 21.68 | 4.72
3776 | 497.2 | 272.2 | 355 | 22.95 | 5.56
3777 | 638.9 | 327.8 | 389 | 24.06 | 5
3778 | 786.1 | 463.9 | 351.4 | 25.38 | 7.22
3779 | 872.2 | 333.3 | 551.1 | 26.45 | 5.56
3780 | 855.6 | 150 | 721.6 | 27.54 | 6.67
3781 | 775 | 144.4 | 687.6 | 27.89 | 6.67
3782 | 625 | 169.4 | 569.6 | 28.09 | 5.56
3783 | 452.8 | 113.9 | 534.6 | 27.68 | 5
3784 | 238.9 | 88.9 | 348.3 | 27.38 | 3.89
3785 | 36.1 | 41.7 | 0 | 26.04 | 4.44
3786 | 0 | 0 | 0 | 27.8 | 3.89
3787 | 0 | 0 | 0 | 26.8 | 2.22
3788 | 0 | 0 | 0 | 26 | 1.11
3789 | 0 | 0 | 0 | 25.3 | 5.28
3790 | 0 | 0 | 0 | 24.4 | 6.11
3791 | 0 | 0 | 0 | 23.8 | 5.56
3792 | 0 | 0 | 0 | 22.8 | 2.22
3793 | 0 | 0 | 0 | 22.3 | 6.39
3794 | 0 | 0 | 0 | 22.3 | 6.67
3795 | 0 | 0 | 0 | 21.3 | 7.22
3796 | 0 | 0 | 0 | 21.3 | 5.83
3797 | 19.4 | 11.1 | 0 | 20.8 | 5.83
3798 | 169.4 | 100 | 339.9 | 21.3 | 5.56
3799 | 338.9 | 163.9 | 406.2 | 22.8 | 5.56
3800 | 497.2 | 244.4 | 398.8 | 24.8 | 5
3801 | 602.8 | 311.1 | 364.8 | 25.6 | 6.11
3802 | 730.6 | 319.4 | 448.4 | 27.4 | 7.5
3803 | 811.1 | 291.7 | 531.4 | 28.9 | 6.67
3804 | 811.1 | 233.3 | 591.1 | 29.6 | 5
3805 | 786.1 | 222.2 | 615.1 | 30.1 | 4.17
3806 | 677.8 | 188.9 | 611.4 | 31.1 | 4.17
3807 | 527.8 | 152.8 | 591.7 | 31.4 | 3.33
3808 | 300 | 138.9 | 374 | 31.1 | 3.61
3809 | 97.2 | 88.9 | 40.8 | 30.3 | 4.44
3810 | 0 | 2.8 | 0 | 28.1 | 5
3811 | 0 | 0 | 0 | 26.6 | 6.94
3812 | 0 | 0 | 0 | 25.6 | 7.22
3813 | 0 | 0 | 0 | 25.1 | 6.67
3814 | 0 | 0 | 0 | 24 | 8.33
3815 | 0 | 0 | 0 | 23.2 | 8.33
3816 | 0 | 0 | 0 | 22.6 | 2.5
3817 | 0 | 0 | 0 | 22.2 | 8.33
3818 | 0 | 0 | 0 | 22 | 7.78
3819 | 0 | 0 | 0 | 21.6 | 7.78
3820 | 0 | 0 | 0 | 21.1 | 7.78
3821 | 8.3 | 0 | 0 | 20.8 | 6.67
3822 | 125 | 16.7 | 442 | 20.9 | 6.67
3823 | 341.7 | 122.2 | 509.3 | 22.1 | 7.78
3824 | 533.3 | 177.8 | 561 | 24.4 | 7.22
3825 | 680.6 | 269.4 | 514.2 | 25.6 | 6.94
3826 | 722.2 | 388.9 | 363.7 | 26.7 | 8.33
3827 | 636.1 | 502.8 | 136.4 | 27 | 7.5
3828 | 627.8 | 319.4 | 315.5 | 28.4 | 8.33
3829 | 519.4 | 513.9 | 6.1 | 28.9 | 7.78
3830 | 602.8 | 355.6 | 309.2 | 28.8 | 7.78
3831 | 411.1 | 355.6 | 87.7 | 28.5 | 7.22
3832 | 230.6 | 205.6 | 58 | 28.4 | 5.56
3833 | 97.2 | 91.7 | 27.2 | 27.7 | 7.5
3834 | 2.8 | 2.8 | 0 | 26.4 | 6.39
3835 | 0 | 0 | 0 | 25.4 | 5.56
3836 | 0 | 0 | 0 | 24.3 | 5.83
3837 | 0 | 0 | 0 | 24.4 | 6.11
3838 | 0 | 0 | 0 | 23 | 3.89
3839 | 0 | 0 | 0 | 22.4 | 3.89
3840 | 0 | 0 | 0 | 21.8 | 2.78
3841 | 0 | 0 | 0 | 21.2 | 4.44
3842 | 0 | 0 | 0 | 20.7 | 3.89
3843 | 0 | 0 | 0 | 20.4 | 3.33
3844 | 0 | 0 | 0 | 20.4 | 3.33
3845 | 0 | 0 | 0 | 19.7 | 4.44
3846 | 105.6 | 22.2 | 406.9 | 19.9 | 3.06
3847 | 261.1 | 111.1 | 348.1 | 21.4 | 5
3848 | 486.1 | 202.8 | 447.1 | 23.8 | 5.56
3849 | 597.2 | 263.9 | 417 | 25.8 | 6.11
3850 | 800 | 250 | 600.2 | 27 | 6.11
3851 | 830.6 | 286.1 | 557.3 | 28.5 | 6.39
3852 | 777.8 | 294.4 | 494.7 | 29.5 | 5.56
3853 | 663.9 | 377.8 | 312.2 | 30.5 | 6.11
3854 | 555.6 | 286.1 | 337.1 | 30.5 | 5.56
3855 | 441.7 | 205.6 | 372.6 | 31 | 5
3856 | 202.8 | 116.7 | 199.8 | 31 | 3.89
3857 | 58.3 | 22.2 | 176.3 | 28.5 | 3.89
3858 | 0 | 0 | 0 | 26 | 2.22
3859 | 0 | 0 | 0 | 21.2 | 4.44
3860 | 0 | 0 | 0 | 20.7 | 6.11
3861 | 0 | 0 | 0 | 21.2 | 3.89
3862 | 0 | 0 | 0 | 21.8 | 2.78
3863 | 0 | 0 | 0 | 22.1 | 3.33
3864 | 0 | 0 | 0 | 22 | 3.06
3865 | 0 | 0 | 0 | 21.9 | 3.33
3866 | 0 | 0 | 0 | 21.6 | 3.61
3867 | 0 | 0 | 0 | 21.3 | 3.89
3868 | 0 | 0 | 0 | 21.1 | 4.44
3869 | 8.3 | 0 | 0 | 20.9 | 3.89
3870 | 175 | 52.8 | 442.9 | 21.1 | 3.89
3871 | 291.7 | 152.8 | 322.2 | 22.8 | 3.89
3872 | 527.8 | 230.6 | 469 | 23.5 | 5
3873 | 688.9 | 205.6 | 604.8 | 25 | 5.56
3874 | 769.4 | 233.3 | 585.1 | 26.6 | 5
3875 | 808.3 | 361.1 | 457.9 | 28.4 | 5.56
3876 | 850 | 197.2 | 668.3 | 29 | 5.56
3877 | 822.2 | 175 | 706.4 | 29.5 | 5
3878 | 708.3 | 158.3 | 688.2 | 30.4 | 5.56
3879 | 508.3 | 161.1 | 547.9 | 31 | 4.17
3880 | 180.6 | 130.6 | 116 | 30.8 | 3.89
3881 | 58.3 | 44.4 | 67.8 | 28.5 | 4.44
3882 | 11.1 | 11.1 | 0 | 27.4 | 1.67
3883 | 0 | 0 | 0 | 24.5 | 3.89
3884 | 0 | 0 | 0 | 22.8 | 8.33
3885 | 0 | 0 | 0 | 22.5 | 5
3886 | 0 | 0 | 0 | 22.5 | 5
3887 | 0 | 0 | 0 | 22.4 | 3.33
3888 | 0 | 0 | 0 | 22.3 | 3.33
3889 | 0 | 0 | 0 | 22 | 4.17
3890 | 0 | 0 | 0 | 21.8 | 4.17
3891 | 0 | 0 | 0 | 21.5 | 5
3892 | 0 | 0 | 0 | 21.5 | 3.89
3893 | 5.6 | 8.3 | 0 | 21 | 3.89
3894 | 91.7 | 77.8 | 67.7 | 21.4 | 3.33
3895 | 344.4 | 122.2 | 515.5 | 23 | 4.17
3896 | 513.9 | 172.2 | 539.2 | 24.2 | 4.44
3897 | 700 | 188.9 | 639.6 | 25.4 | 5.56
3898 | 722.2 | 225 | 542.8 | 27.3 | 4.44
3899 | 847.2 | 255.6 | 605.9 | 28.5 | 4.44
3900 | 816.7 | 275 | 554.7 | 29.7 | 3.89
3901 | 833.3 | 241.7 | 645.9 | 30.5 | 5
3902 | 686.1 | 236.1 | 563.1 | 31 | 3.89
3903 | 433.3 | 200 | 368.2 | 31 | 3.89
3904 | 358.3 | 150 | 483.2 | 31 | 3.89
3905 | 133.3 | 113.9 | 94.8 | 31.2 | 3.33
3906 | 2.8 | 30.6 | 0 | 28.2 | 3.89
3907 | 0 | 0 | 0 | 27.4 | 3.61
3908 | 0 | 0 | 0 | 27 | 3.06
3909 | 0 | 0 | 0 | 26.2 | 2.78
3910 | 0 | 0 | 0 | 24.7 | 5.56
3911 | 0 | 0 | 0 | 24 | 5.83
3912 | 0 | 0 | 0 | 23.2 | 3.61
3913 | 0 | 0 | 0 | 22.8 | 6.11
3914 | 0 | 0 | 0 | 22.2 | 5.28
3915 | 0 | 0 | 0 | 21.5 | 5
3916 | 0 | 0 | 0 | 21 | 3.33
3917 | 5.6 | 0 | 0 | 20.9 | 3.33
3918 | 55.6 | 77.8 | 0 | 21.8 | 4.72
3919 | 169.4 | 183.3 | 0 | 22.1 | 4.72
3920 | 291.7 | 261.1 | 48.2 | 24.5 | 5.56
3921 | 263.9 | 263.9 | 0 | 25.9 | 5.56
3922 | 594.4 | 477.8 | 127.4 | 26.2 | 4.72
3923 | 725 | 366.7 | 367 | 27.6 | 4.44
3924 | 866.7 | 286.1 | 594.6 | 28.4 | 4.44
3925 | 733.3 | 400 | 364 | 29.2 | 4.44
3926 | 683.3 | 316.7 | 458.9 | 30 | 3.89
3927 | 436.1 | 269.4 | 263 | 30.2 | 3.33
3928 | 219.4 | 211.1 | 19.3 | 30.2 | 3.89
3929 | 50 | 91.7 | 0 | 29 | 3.06
3930 | 0 | 8.3 | 0 | 28.2 | 3.33
3931 | 0 | 0 | 0 | 23.2 | 2.78
3932 | 0 | 0 | 0 | 22.7 | 11.11
3933 | 0 | 0 | 0 | 23.5 | 6.39
3934 | 0 | 0 | 0 | 23.7 | 4.44
3935 | 0 | 0 | 0 | 21.7 | 1.94
3936 | 0 | 0 | 0 | 21.47 | 3.89
3937 | 0 | 0 | 0 | 21.18 | 3.89
3938 | 0 | 0 | 0 | 20.95 | 3.89
3939 | 0 | 0 | 0 | 20.72 | 2.22
3940 | 0 | 0 | 0 | 20.61 | 4.17
3941 | 2.8 | 0 | 0 | 20.39 | 3.33
3942 | 50 | 8.3 | 202.8 | 20.63 | 3.06
3943 | 86.1 | 66.7 | 45.1 | 21.68 | 5
3944 | 311.1 | 263.9 | 74.5 | 22.95 | 5.56
3945 | 480.6 | 433.3 | 59.1 | 24.06 | 6.11
3946 | 450 | 386.1 | 240.5 | 25.38 | 3.89
3947 | 513.9 | 413.8 | 298.5 | 26.45 | 1.67
3948 | 716.7 | 544.4 | 176.4 | 27.54 | 2.5
3949 | 643.7 | 380.9 | 326.2 | 27.89 | 1.67
3950 | 519.4 | 211.1 | 386 | 28.09 | 3.33
3951 | 356.7 | 240.8 | 230 | 27.68 | 2.78
3952 | 207.4 | 153 | 160.6 | 27.38 | 4.17
3953 | 71.3 | 63.6 | 84.8 | 26.04 | 4.44
3954 | 3 | 4.8 | 0 | 24.9 | 3.33
3955 | 0 | 0 | 0 | 24.8 | 1.67
3956 | 0 | 0 | 0 | 24.6 | 1.39
3957 | 0 | 0 | 0 | 24 | 2.78
3958 | 0 | 0 | 0 | 24.3 | 2.78
3959 | 0 | 0 | 0 | 23.1 | 4.44
3960 | 0 | 0 | 0 | 22.4 | 4.17
3961 | 0 | 0 | 0 | 21.7 | 4.44
3962 | 0 | 0 | 0 | 21.5 | 5
3963 | 0 | 0 | 0 | 21.4 | 5
3964 | 0 | 0 | 0 | 21.1 | 4.44
3965 | 11.1 | 0 | 0 | 21.1 | 6.11
3966 | 88.9 | 27.8 | 297.2 | 21.1 | 6.11
3967 | 288.9 | 119.4 | 392.9 | 22.1 | 6.11
3968 | 283.3 | 236.1 | 74.5 | 23.5 | 6.94
3969 | 391.7 | 325 | 83.5 | 23.8 | 6.67
3970 | 425 | 444.4 | 0 | 24.3 | 6.11
3971 | 672.2 | 463.9 | 213.4 | 24.7 | 6.11
3972 | 819.4 | 391.7 | 438.3 | 27.1 | 6.39
3973 | 725 | 430.6 | 321.6 | 27.7 | 6.11
3974 | 533.3 | 375 | 198.2 | 27.7 | 7.22
3975 | 356.7 | 240.8 | 230 | 27.7 | 7.22
3976 | 207.4 | 153 | 160.6 | 27.4 | 7.78
3977 | 71.3 | 63.6 | 84.8 | 26.3 | 6.67
3978 | 3 | 4.8 | 0 | 25 | 7.78
3979 | 0 | 0 | 0 | 24 | 7.78
3980 | 0 | 0 | 0 | 22.4 | 2.22
3981 | 0 | 0 | 0 | 22 | 10
3982 | 0 | 0 | 0 | 21.5 | 8.33
3983 | 0 | 0 | 0 | 20.8 | 7.78
3984 | 0 | 0 | 0 | 20.7 | 4.44
3985 | 0 | 0 | 0 | 20.5 | 8.33
3986 | 0 | 0 | 0 | 20.3 | 7.78
3987 | 0 | 0 | 0 | 20.2 | 6.67
3988 | 0 | 0 | 0 | 19.9 | 7.22
3989 | 2.8 | 0 | 0 | 19.7 | 6.11
3990 | 47.2 | 47.2 | 0 | 20 | 6.67
3991 | 163.9 | 172.2 | 0 | 20.9 | 6.11
3992 | 263.9 | 252.8 | 17.5 | 21.5 | 6.67
3993 | 416.7 | 377.8 | 48.7 | 22.9 | 7.78
3994 | 358.3 | 352.8 | 6.1 | 24.2 | 8.33
3995 | 511.1 | 508.3 | 2.8 | 25.2 | 8.89
3996 | 572.2 | 516.7 | 56.9 | 26.6 | 7.78
3997 | 611.1 | 530.6 | 88 | 27 | 7.5
3998 | 386.1 | 408.3 | 0 | 26.8 | 7.22
3999 | 350 | 341.7 | 13.2 | 26.3 | 6.67
4000 | 261.1 | 247.2 | 32.2 | 26.2 | 6.67
4001 | 119.4 | 116.7 | 13.5 | 23.6 | 7.22
4002 | 11.1 | 16.7 | 0 | 22.9 | 6.11
4003 | 0 | 0 | 0 | 22.1 | 5
4004 | 0 | 0 | 0 | 21.6 | 5
4005 | 0 | 0 | 0 | 20.6 | 5
4006 | 0 | 0 | 0 | 20.5 | 5.56
4007 | 0 | 0 | 0 | 20.4 | 6.11
4008 | 0 | 0 | 0 | 20 | 4.72
4009 | 0 | 0 | 0 | 20.1 | 6.94
4010 | 0 | 0 | 0 | 19.7 | 5.56
4011 | 0 | 0 | 0 | 19 | 5
4012 | 0 | 0 | 0 | 18.9 | 5.56
4013 | 2.8 | 0 | 0 | 18.7 | 5.56
4014 | 52.8 | 0 | 256.4 | 19 | 5.56
4015 | 200 | 50 | 347.7 | 19.7 | 5.56
4016 | 427.8 | 358.3 | 109.6 | 21.3 | 6.11
4017 | 541.7 | 438.9 | 128.7 | 23.5 | 6.39
4018 | 544.4 | 447.2 | 106.2 | 25.5 | 7.22
4019 | 630.6 | 633.3 | 0 | 25.1 | 8.33
4020 | 522.2 | 547.2 | 0 | 26.1 | 5
4021 | 666.7 | 458.3 | 227.6 | 26.9 | 7.22
4022 | 391.7 | 369.4 | 27.8 | 26.9 | 6.67
4023 | 308.3 | 308.3 | 0 | 25.8 | 5.56
4024 | 136.1 | 141.7 | 0 | 25.1 | 8.33
4025 | 52.8 | 58.3 | 0 | 21.5 | 7.78
4026 | 2.8 | 5.6 | 0 | 20.8 | 9.17
4027 | 0 | 0 | 0 | 20.6 | 9.17
4028 | 0 | 0 | 0 | 20.3 | 5.56
4029 | 0 | 0 | 0 | 20.3 | 5.83
4030 | 0 | 0 | 0 | 19.8 | 5.56
4031 | 0 | 0 | 0 | 19.6 | 5
4032 | 0 | 0 | 0 | 19.6 | 5
4033 | 0 | 0 | 0 | 19.4 | 5.56
4034 | 0 | 0 | 0 | 19.5 | 6.94
4035 | 0 | 0 | 0 | 19.4 | 6.39
4036 | 0 | 0 | 0 | 19.3 | 6.67
4037 | 5.6 | 2.8 | 0 | 19.3 | 7.22
4038 | 77.8 | 77.8 | 0 | 19.5 | 7.78
4039 | 222.2 | 227.8 | 0 | 20.7 | 7.22
4040 | 333.3 | 319.4 | 21.9 | 22 | 8.33
4041 | 338.9 | 355.6 | 0 | 22.4 | 8.61
4042 | 427.8 | 419.4 | 9.1 | 23.8 | 8.33
4043 | 422.2 | 461.1 | 0 | 25.1 | 7.22
4044 | 602.8 | 569.4 | 34.2 | 26.8 | 7.78
4045 | 375 | 386.1 | 0 | 25.8 | 9.44
4046 | 438.9 | 408.3 | 38.3 | 25.3 | 7.78
4047 | 372.2 | 327.8 | 70.2 | 25.5 | 7.78
4048 | 219.4 | 177.8 | 96.6 | 25.7 | 6.94
4049 | 75 | 55.6 | 94.4 | 25 | 7.5
4050 | 2.8 | 0 | 0 | 23.9 | 7.22
4051 | 0 | 0 | 0 | 23.1 | 5
4052 | 0 | 0 | 0 | 22.6 | 6.67
4053 | 0 | 0 | 0 | 21.8 | 6.11
4054 | 0 | 0 | 0 | 21.5 | 6.67
4055 | 0 | 0 | 0 | 21 | 6.11
4056 | 0 | 0 | 0 | 20.8 | 5.28
4057 | 0 | 0 | 0 | 20.3 | 5.56
4058 | 0 | 0 | 0 | 19.6 | 6.39
4059 | 0 | 0 | 0 | 19.7 | 5.56
4060 | 0 | 0 | 0 | 19.8 | 7.22
4061 | 2.8 | 2.8 | 0 | 19.7 | 7.22
4062 | 69.4 | 83.3 | 0 | 20.1 | 6.11
4063 | 161.1 | 166.7 | 0 | 20.8 | 5.56
4064 | 302.8 | 280.6 | 35.1 | 22 | 6.67
4065 | 494.4 | 427.8 | 83.5 | 23.7 | 7.22
4066 | 455.6 | 463.9 | 0 | 26 | 6.67
4067 | 747.2 | 458.3 | 296.1 | 26 | 8.06
4068 | 508.3 | 497.2 | 11.4 | 26 | 6.39
4069 | 652.8 | 522.2 | 142.6 | 27.1 | 6.67
4070 | 536.1 | 430.6 | 132.2 | 27.7 | 8.33
4071 | 180.6 | 188.9 | 0 | 25.6 | 9.17
4072 | 216.7 | 202.8 | 32.2 | 25.5 | 6.67
4073 | 50 | 66.7 | 0 | 23.2 | 6.94
4074 | 0 | 0 | 0 | 22.4 | 9.72
4075 | 0 | 0 | 0 | 22 | 8.06
4076 | 0 | 0 | 0 | 21.4 | 7.22
4077 | 0 | 0 | 0 | 21 | 6.67
4078 | 0 | 0 | 0 | 20.6 | 8.33
4079 | 0 | 0 | 0 | 20.2 | 6.67
4080 | 0 | 0 | 0 | 20.2 | 5.56
4081 | 0 | 0 | 0 | 20.2 | 6.94
4082 | 0 | 0 | 0 | 20 | 6.67
4083 | 0 | 0 | 0 | 19.7 | 6.39
4084 | 0 | 0 | 0 | 19.6 | 5
4085 | 0 | 0 | 0 | 19.3 | 5.56
4086 | 58.3 | 69.4 | 0 | 19.2 | 5.56
4087 | 180.6 | 191.7 | 0 | 19.7 | 5.56
4088 | 222.2 | 225 | 0 | 20.2 | 6.11
4089 | 283.3 | 266.7 | 20.9 | 22.2 | 6.39
4090 | 444.4 | 427.8 | 18.2 | 23.8 | 7.22
4091 | 419.4 | 436.1 | 0 | 25.2 | 8.89
4092 | 408.3 | 441.7 | 0 | 25.7 | 7.22
4093 | 330.6 | 308.3 | 24.3 | 25.7 | 9.44
4094 | 250 | 286.1 | 0 | 25.6 | 8.33
4095 | 236.1 | 250 | 0 | 24.6 | 8.33
4096 | 136.1 | 141.7 | 0 | 24.4 | 6.11
4097 | 44.4 | 58.3 | 0 | 23.7 | 6.11
4098 | 0 | 0 | 0 | 23.2 | 7.22
4099 | 0 | 0 | 0 | 22.8 | 6.67
4100 | 0 | 0 | 0 | 22.2 | 7.22
4101 | 0 | 0 | 0 | 21.8 | 5.83
4102 | 0 | 0 | 0 | 21.7 | 5.56
4103 | 0 | 0 | 0 | 21.4 | 5.56
4104 | 0 | 0 | 0 | 21.47 | 5.83
4105 | 0 | 0 | 0 | 21.18 | 5.28
4106 | 0 | 0 | 0 | 20.95 | 6.11
4107 | 0 | 0 | 0 | 20.72 | 6.39
4108 | 0 | 0 | 0 | 20.61 | 6.11
4109 | 0 | 0 | 0 | 20.39 | 5.56
4110 | 66.7 | 36.1 | 148.3 | 20.63 | 5
4111 | 275 | 150 | 289.7 | 21.68 | 5.83
4112 | 433.3 | 305.6 | 201.7 | 22.95 | 6.39
4113 | 638.9 | 380.6 | 323.5 | 24.06 | 6.67
4114 | 577.8 | 411.1 | 182.1 | 25.38 | 8.33
4115 | 530.6 | 452.8 | 79.7 | 26.45 | 8.89
4116 | 733.3 | 444.4 | 296.1 | 27.54 | 8.33
4117 | 727.8 | 344.4 | 418.8 | 27.89 | 8.61
4118 | 530.6 | 302.8 | 285.2 | 28.09 | 8.33
4119 | 356.7 | 191.7 | 230 | 27.68 | 7.78
4120 | 207.4 | 122.2 | 160.6 | 27.38 | 7.78
4121 | 71.3 | 41.7 | 84.8 | 26.04 | 8.33
4122 | 3 | 0 | 0 | 24.7 | 8.33
4123 | 0 | 0 | 0 | 24.1 | 5
4124 | 0 | 0 | 0 | 23.5 | 6.11
4125 | 0 | 0 | 0 | 22.7 | 6.67
4126 | 0 | 0 | 0 | 22.4 | 6.39
4127 | 0 | 0 | 0 | 21.7 | 5
4128 | 0 | 0 | 0 | 21.47 | 6.11
4129 | 0 | 0 | 0 | 21.18 | 5.56
4130 | 0 | 0 | 0 | 20.95 | 5
4131 | 0 | 0 | 0 | 20.72 | 5.56
4132 | 0 | 0 | 0 | 20.61 | 5
4133 | 8.3 | 27.8 | 0 | 20.39 | 6.11
4134 | 72.2 | 77.8 | 0 | 20.63 | 5.56
4135 | 191.7 | 211.1 | 0 | 21.68 | 6.11
4136 | 441.7 | 369.4 | 114 | 22.95 | 6.67
4137 | 436.1 | 377.8 | 73 | 24.06 | 6.11
4138 | 547.2 | 425 | 133.5 | 25.38 | 6.67
4139 | 680.6 | 447.2 | 239.2 | 26.45 | 7.22
4140 | 441.7 | 297.2 | 148 | 27.54 | 7.78
4141 | 580.6 | 494.4 | 94.1 | 27.89 | 7.78
4142 | 630.6 | 294.4 | 420.9 | 28.09 | 7.78
4143 | 266.7 | 175 | 144.7 | 27.68 | 3.33
4144 | 125 | 113.9 | 25.8 | 27.38 | 5.56
4145 | 66.7 | 66.7 | 0 | 26.04 | 4.44
4146 | 0 | 0 | 0 | 24.4 | 6.11
4147 | 0 | 0 | 0 | 21.1 | 6.11
4148 | 0 | 0 | 0 | 20.9 | 6.67
4149 | 0 | 0 | 0 | 20.9 | 3.89
4150 | 0 | 0 | 0 | 21 | 3.61
4151 | 0 | 0 | 0 | 20.9 | 2.78
4152 | 0 | 0 | 0 | 20.9 | 6.39
4153 | 0 | 0 | 0 | 20.9 | 4.44
4154 | 0 | 0 | 0 | 20.7 | 5
4155 | 0 | 0 | 0 | 20.7 | 5
4156 | 0 | 0 | 0 | 20.7 | 5
4157 | 0 | 0 | 0 | 20.5 | 5.56
4158 | 50 | 55.6 | 0 | 20.6 | 5
4159 | 233.3 | 216.7 | 38.6 | 21.1 | 6.11
4160 | 550 | 386.1 | 258.7 | 22.3 | 6.11
4161 | 388.9 | 336.1 | 66.1 | 24.5 | 7.22
4162 | 319.4 | 313.9 | 6.1 | 24.7 | 8.33
4163 | 650 | 400 | 256.2 | 26.4 | 6.67
4164 | 422.2 | 302.8 | 122.4 | 27.3 | 6.67
4165 | 694.4 | 380.6 | 342.9 | 27.7 | 7.78
4166 | 422.2 | 363.9 | 73 | 26.2 | 7.22
4167 | 369.4 | 319.4 | 78.9 | 24.4 | 9.44
4168 | 161.1 | 158.3 | 6.4 | 24.3 | 6.67
4169 | 72.2 | 66.7 | 27 | 24.8 | 6.67
4170 | 2.8 | 2.8 | 0 | 22.7 | 7.78
4171 | 0 | 0 | 0 | 22.3 | 6.11
4172 | 0 | 0 | 0 | 21.7 | 5
4173 | 0 | 0 | 0 | 21.5 | 4.72
4174 | 0 | 0 | 0 | 21.3 | 3.89
4175 | 0 | 0 | 0 | 21.3 | 3.89
4176 | 0 | 0 | 0 | 21.2 | 6.67
4177 | 0 | 0 | 0 | 20.7 | 5.56
4178 | 0 | 0 | 0 | 20.7 | 5.28
4179 | 0 | 0 | 0 | 20.5 | 6.67
4180 | 0 | 0 | 0 | 20.5 | 6.11
4181 | 5.6 | 0 | 0 | 20.3 | 5.56
4182 | 47.2 | 63.9 | 0 | 20.4 | 6.11
4183 | 150 | 152.8 | 0 | 20.8 | 5.56
4184 | 141.7 | 138.9 | 4.4 | 22.2 | 4.44
4185 | 505.2 | 329.4 | 248.8 | 21.3 | 6.11
4186 | 494.4 | 475 | 21.2 | 22.1 | 6.67
4187 | 550 | 519.4 | 31.3 | 23.5 | 5.56
4188 | 719.4 | 644.4 | 76.9 | 25.1 | 8.33
4189 | 411.1 | 425 | 0 | 24.3 | 7.78
4190 | 341.7 | 325 | 20.9 | 25.8 | 7.22
4191 | 280.6 | 283.3 | 0 | 25.1 | 8.33
4192 | 125 | 147.2 | 0 | 25.2 | 7.22
4193 | 66.7 | 52.8 | 67.5 | 24.4 | 5
4194 | 2.8 | 0 | 0 | 23.4 | 7.22
4195 | 0 | 0 | 0 | 22.8 | 5.56
4196 | 0 | 0 | 0 | 22.3 | 5
4197 | 0 | 0 | 0 | 21.8 | 5.56
4198 | 0 | 0 | 0 | 21.8 | 5
4199 | 0 | 0 | 0 | 21.8 | 4.44
4200 | 0 | 0 | 0 | 21.8 | 6.94
4201 | 0 | 0 | 0 | 21.7 | 4.44
4202 | 0 | 0 | 0 | 21.3 | 5.56
4203 | 0 | 0 | 0 | 21.3 | 5
4204 | 0 | 0 | 0 | 21.3 | 4.44
4205 | 19.4 | 8.3 | 0 | 20.8 | 4.17
4206 | 127.8 | 88.9 | 188.9 | 20.8 | 3.89
4207 | 180.6 | 161.1 | 45.1 | 21.8 | 3.89
4208 | 383.3 | 330.6 | 83.3 | 23.3 | 5.56
4209 | 538.9 | 402.8 | 170.4 | 24 | 6.11
4210 | 519.4 | 477.8 | 45.5 | 25.6 | 5
4211 | 525 | 519.4 | 5.7 | 26.7 | 7.22
4212 | 683.3 | 480.6 | 207.8 | 27.8 | 5.56
4213 | 658.3 | 438.9 | 239.7 | 27.5 | 7.22
4214 | 516.7 | 336.1 | 226.1 | 29 | 7.22
4215 | 352.8 | 286.1 | 105.2 | 26.9 | 6.67
4216 | 230.6 | 200 | 70.8 | 27 | 7.78
4217 | 94.4 | 63.9 | 148.4 | 25.3 | 6.67
4218 | 11.1 | 11.1 | 0 | 24 | 8.33
4219 | 0 | 0 | 0 | 23 | 6.11
4220 | 0 | 0 | 0 | 22.5 | 6.67
4221 | 0 | 0 | 0 | 22.1 | 5.56
4222 | 0 | 0 | 0 | 22 | 6.11
4223 | 0 | 0 | 0 | 21.9 | 5.56
4224 | 0 | 0 | 0 | 21.6 | 7.22
4225 | 0 | 0 | 0 | 21.1 | 3.89
4226 | 0 | 0 | 0 | 21 | 4.44
4227 | 0 | 0 | 0 | 21 | 3.89
4228 | 0 | 0 | 0 | 21 | 3.33
4229 | 11.1 | 11.1 | 0 | 21 | 3.89
4230 | 86.1 | 97.2 | 0 | 21 | 3.89
4231 | 213.9 | 202.8 | 25.8 | 21.6 | 3.89
4232 | 313.9 | 311.1 | 4.4 | 22.4 | 5
4233 | 497.2 | 450 | 59.1 | 23.8 | 5
4234 | 552.8 | 505.6 | 51.6 | 25.2 | 5.56
4235 | 494.4 | 469.4 | 25.6 | 26.2 | 6.67
4236 | 572.2 | 513.9 | 59.8 | 28.1 | 7.78
4237 | 636.1 | 458.3 | 194.2 | 27.8 | 7.22
4238 | 600 | 369.4 | 288.7 | 28.7 | 8.61
4239 | 344.4 | 305.6 | 61.4 | 25.2 | 6.67
4240 | 205.6 | 186.1 | 45.1 | 26.5 | 6.11
4241 | 83.3 | 75 | 40.5 | 26.2 | 5.56
4242 | 5.6 | 5.6 | 0 | 24.7 | 6.67
4243 | 0 | 0 | 0 | 24.1 | 3.33
4244 | 0 | 0 | 0 | 23.6 | 3.89
4245 | 0 | 0 | 0 | 22.9 | 3.89
4246 | 0 | 0 | 0 | 22.2 | 4.72
4247 | 0 | 0 | 0 | 21.7 | 4.44
4248 | 0 | 0 | 0 | 22.2 | 7.5
4249 | 0 | 0 | 0 | 21 | 3.89
4250 | 0 | 0 | 0 | 20.6 | 4.44
4251 | 0 | 0 | 0 | 20.6 | 3.89
4252 | 0 | 0 | 0 | 20.7 | 5
4253 | 6.6 | 19.4 | 0 | 20.6 | 5.56
4254 | 88.2 | 91.7 | 217.7 | 20.7 | 5.56
4255 | 238.7 | 208.3 | 296.3 | 22.6 | 5.56
4256 | 390.3 | 366.7 | 237.3 | 22.5 | 5.56
4257 | 522.2 | 438.9 | 104.3 | 23.8 | 5.56
4258 | 616.7 | 463.9 | 166.9 | 25 | 6.11
4259 | 561.1 | 494.4 | 68.3 | 26.6 | 6.67
4260 | 683.3 | 522.2 | 165.1 | 27.2 | 7.78
4261 | 502.8 | 469.4 | 36.4 | 26.5 | 7.78
4262 | 316.7 | 336.1 | 0 | 26.7 | 10.56
4263 | 394.4 | 350 | 70.1 | 26.7 | 6.67
4264 | 194.4 | 180.6 | 32.2 | 23.8 | 6.67
4265 | 41.7 | 75 | 0 | 21.7 | 5
4266 | 2.8 | 13.9 | 0 | 21.8 | 6.67
4267 | 0 | 0 | 0 | 21.5 | 2.78
4268 | 0 | 0 | 0 | 21.4 | 3.89
4269 | 0 | 0 | 0 | 21.3 | 3.33
4270 | 0 | 0 | 0 | 22.2 | 4.44
4271 | 0 | 0 | 0 | 20.7 | 3.89
4272 | 0 | 0 | 0 | 20.6 | 7.78
4273 | 0 | 0 | 0 | 20.6 | 5
4274 | 0 | 0 | 0 | 20.3 | 3.89
4275 | 0 | 0 | 0 | 20.3 | 4.44
4276 | 0 | 0 | 0 | 20.3 | 3.89
4277 | 5.6 | 5.6 | 0 | 20.3 | 3.89
4278 | 80.6 | 94.4 | 0 | 20.4 | 5
4279 | 202.8 | 222.2 | 0 | 21.3 | 4.44
4280 | 230.6 | 272.2 | 0 | 21.7 | 5
4281 | 375 | 391.7 | 0 | 22.1 | 6.11
4282 | 567.4 | 386.1 | 240.5 | 23.6 | 5.56
4283 | 652.8 | 413.8 | 298.5 | 24 | 6.11
4284 | 686.9 | 390.8 | 328.6 | 23.4 | 7.22
4285 | 643.7 | 380.9 | 326.2 | 24.3 | 9.44
4286 | 550.7 | 306.2 | 360.9 | 21.5 | 7.78
4287 | 211.1 | 213.9 | 0 | 22.9 | 3.89
4288 | 147.2 | 158.3 | 0 | 22.9 | 6.11
4289 | 55.6 | 86.1 | 0 | 21.2 | 6.67
4290 | 3 | 11.1 | 0 | 21.5 | 8.89
4291 | 0 | 0 | 0 | 21.4 | 4.44
4292 | 0 | 0 | 0 | 21 | 4.44
4293 | 0 | 0 | 0 | 20.4 | 4.44
4294 | 0 | 0 | 0 | 21.1 | 5.56
4295 | 0 | 0 | 0 | 19.8 | 5
4296 | 0 | 0 | 0 | 19.5 | 8.06
4297 | 0 | 0 | 0 | 19.5 | 5
4298 | 0 | 0 | 0 | 19.5 | 5.56
4299 | 0 | 0 | 0 | 19.4 | 5
4300 | 0 | 0 | 0 | 19.4 | 5
4301 | 5.6 | 0 | 0 | 19.4 | 5.56
4302 | 52.8 | 44.4 | 40.6 | 19.7 | 6.11
4303 | 313.9 | 222.2 | 212.6 | 20.5 | 6.11
4304 | 344.4 | 327.8 | 26.3 | 22.3 | 6.67
4305 | 391.7 | 386.1 | 7 | 22.8 | 6.67
4306 | 497.2 | 483.3 | 15.2 | 23.8 | 7.22
4307 | 672.2 | 475 | 202 | 25.6 | 6.94
4308 | 761.1 | 402.8 | 367 | 27.1 | 6.11
4309 | 643.7 | 380.9 | 326.2 | 27.2 | 8.33
4310 | 647.2 | 358.3 | 361.6 | 27.3 | 10
4311 | 356.7 | 240.8 | 230 | 26.9 | 6.67
4312 | 207.4 | 153 | 160.6 | 25.9 | 6.94
4313 | 38.9 | 38.9 | 0 | 24.7 | 4.72
4314 | 5.6 | 2.8 | 0 | 23.6 | 6.11
4315 | 0 | 0 | 0 | 23.2 | 6.11
4316 | 0 | 0 | 0 | 21.3 | 5
4317 | 0 | 0 | 0 | 21.4 | 5.56
4318 | 0 | 0 | 0 | 21.1 | 3.89
4319 | 0 | 0 | 0 | 20.7 | 3.89
4320 | 0 | 0 | 0 | 20.5 | 8.33
4321 | 0 | 0 | 0 | 20.2 | 5.56
4322 | 0 | 0 | 0 | 20.1 | 6.39
4323 | 0 | 0 | 0 | 20 | 5.28
4324 | 0 | 0 | 0 | 19.7 | 5.56
4325 | 0 | 2.8 | 0 | 19.6 | 6.11
4326 | 22.2 | 72.2 | 0 | 19.7 | 5.56
4327 | 122.2 | 186.1 | 0 | 20.7 | 6.11
4328 | 219.4 | 277.8 | 0 | 21.9 | 6.67
4329 | 272.2 | 313.9 | 0 | 22.6 | 6.11
4330 | 461.1 | 466.7 | 0 | 23.7 | 5.56
4331 | 608.3 | 413.8 | 298.5 | 25.6 | 6.67
4332 | 686.9 | 390.8 | 328.6 | 27.7 | 5.56
4333 | 643.7 | 380.9 | 326.2 | 27.4 | 6.67
4334 | 550.7 | 306.2 | 360.9 | 27.9 | 5.56
4335 | 356.7 | 240.8 | 230 | 27.6 | 6.11
4336 | 207.4 | 153 | 160.6 | 27.3 | 4.72
4337 | 71.3 | 63.6 | 84.8 | 26.4 | 5
4338 | 3 | 4.8 | 0 | 24.4 | 4.44
4339 | 0 | 0 | 0 | 23.6 | 5.56
4340 | 0 | 0 | 0 | 22.4 | 4.44
4341 | 0 | 0 | 0 | 21.7 | 4.72
4342 | 0 | 0 | 0 | 20.9 | 3.33
4343 | 0 | 0 | 0 | 20.4 | 2.78
4344 | 0 | 0 | 0 | 19.9 | 0.28
4345 | 0 | 0 | 0 | 19.8 | 2.78
4346 | 0 | 0 | 0 | 19.9 | 3.06
4347 | 0 | 0 | 0 | 19.8 | 2.78
4348 | 0 | 0 | 0 | 19.5 | 2.78
4349 | 6.4 | 4.3 | 0 | 19.4 | 2.78
4350 | 96.7 | 77.7 | 236 | 19.9 | 1.94
4351 | 247.4 | 195.2 | 168.9 | 20.9 | 2.78
4352 | 417.6 | 294.6 | 240.4 | 23.5 | 2.78
4353 | 528.8 | 370 | 234.5 | 25 | 4.44
4354 | 761.1 | 172.2 | 642.8 | 26 | 4.44
4355 | 763.9 | 277.8 | 497.7 | 27.5 | 4.44
4356 | 602.8 | 430.6 | 176.3 | 29 | 4.17
4357 | 727.8 | 288.9 | 479.1 | 29.2 | 5.56
4358 | 577.8 | 222.2 | 444.9 | 29.5 | 4.72
4359 | 408.3 | 230.6 | 280.5 | 29.7 | 5
4360 | 222.2 | 152.8 | 161.1 | 29.3 | 5
4361 | 83.3 | 69.4 | 67.7 | 28.7 | 5
4362 | 5.6 | 5.6 | 0 | 28.2 | 4.44
4363 | 0 | 0 | 0 | 26 | 3.33
4364 | 0 | 0 | 0 | 24.5 | 5
4365 | 0 | 0 | 0 | 23.8 | 3.33
4366 | 0 | 0 | 0 | 23 | 4.44
4367 | 0 | 0 | 0 | 22.5 | 3.33
4368 | 0 | 0 | 0 | 22 | 0.56
4369 | 0 | 0 | 0 | 21.7 | 3.33
4370 | 0 | 0 | 0 | 21.2 | 2.78
4371 | 0 | 0 | 0 | 20.7 | 2.78
4372 | 0 | 0 | 0 | 20.5 | 2.22
4373 | 11.1 | 0 | 0 | 20.5 | 1.67
4374 | 161.1 | 91.7 | 338.9 | 20.8 | 2.78
4375 | 238.9 | 222.2 | 38.7 | 22 | 3.06
4376 | 413.9 | 319.4 | 149 | 22.6 | 4.44
4377 | 461.1 | 419.4 | 52.1 | 23.6 | 2.22
4378 | 572.2 | 522.2 | 54.6 | 25.1 | 2.78
4379 | 600 | 522.2 | 79.6 | 26.6 | 3.33
4380 | 644.4 | 475 | 173.5 | 27.7 | 3.89
4381 | 725 | 419.4 | 333.5 | 28.6 | 2.78
4382 | 594.4 | 355.6 | 298.9 | 29.3 | 2.78
4383 | 208.3 | 194.4 | 21.9 | 29.1 | 2.78
4384 | 136.1 | 150 | 0 | 29.4 | 5
4385 | 47.2 | 75 | 0 | 27.8 | 3.33
4386 | 0 | 5.6 | 0 | 26 | 4.44
4387 | 0 | 0 | 0 | 23.6 | 1.67
4388 | 0 | 0 | 0 | 23.6 | 3.33
4389 | 0 | 0 | 0 | 23.6 | 1.11
4390 | 0 | 0 | 0 | 23.6 | 1.11
4391 | 0 | 0 | 0 | 23.4 | 1.39
4392 | 0 | 0 | 0 | 22.8 | 0.83
4393 | 0 | 0 | 0 | 22.6 | 2.78
4394 | 0 | 0 | 0 | 22.2 | 3.33
4395 | 0 | 0 | 0 | 21.7 | 2.22
4396 | 0 | 0 | 0 | 21.6 | 2.78
4397 | 19.4 | 0 | 0 | 21.1 | 2.78
4398 | 83.3 | 55.6 | 135.7 | 21.4 | 2.78
4399 | 258.3 | 122.2 | 315.9 | 22.4 | 2.78
4400 | 594.4 | 191.7 | 635.5 | 24.6 | 2.78
4401 | 727.8 | 166.7 | 701.9 | 25.6 | 2.78
4402 | 855.6 | 322.2 | 581.9 | 27.7 | 2.22
4403 | 794.4 | 347.2 | 457.7 | 28.3 | 2.22
4404 | 586.1 | 408.3 | 181.9 | 28.9 | 2.22
4405 | 458.3 | 291.7 | 181.9 | 25.3 | 1.67
4406 | 155.6 | 177.8 | 0 | 25.3 | 0
4407 | 222.2 | 213.9 | 13.1 | 27.3 | 2.22
4408 | 155.6 | 144.4 | 25.8 | 29.1 | 1.11
4409 | 61.1 | 61.1 | 0 | 28.7 | 1.11
4410 | 5.6 | 16.7 | 0 | 27.8 | 1.11
4411 | 0 | 0 | 0 | 26.9 | 0.83
4412 | 0 | 0 | 0 | 25.7 | 0
4413 | 0 | 0 | 0 | 24.8 | 0.56
4414 | 0 | 0 | 0 | 24.8 | 0
4415 | 0 | 0 | 0 | 24 | 0
4416 | 0 | 0 | 0 | 23.3 | 1.11
4417 | 0 | 0 | 0 | 22.9 | 2.78
4418 | 0 | 0 | 0 | 22.7 | 3.06
4419 | 0 | 0 | 0 | 22.5 | 3.89
4420 | 0 | 0 | 0 | 21.8 | 3.89
4421 | 8.3 | 22.2 | 0 | 21.3 | 3.33
4422 | 86.1 | 125 | 0 | 21.3 | 3.61
4423 | 308.3 | 286.1 | 51.6 | 22.7 | 3.33
4424 | 475 | 327.8 | 232.3 | 23.7 | 3.33
4425 | 711.1 | 347.2 | 455.1 | 25.4 | 4.72
4426 | 780.6 | 325 | 496.9 | 26.7 | 3.89
4427 | 891.7 | 330.6 | 574.1 | 28.4 | 3.33
4428 | 925 | 338.9 | 599.7 | 29.1 | 3.33
4429 | 794.4 | 333.3 | 503 | 29.9 | 3.33
4430 | 694.4 | 380.6 | 392.6 | 30.2 | 4.44
4431 | 477.8 | 338.9 | 219.1 | 30.2 | 3.33
4432 | 269.4 | 213.9 | 129 | 29.1 | 3.33
4433 | 63.9 | 61.1 | 13.6 | 28.9 | 3.89
4434 | 0 | 0 | 0 | 26.2 | 3.33
4435 | 0 | 0 | 0 | 24.7 | 3.89
4436 | 0 | 0 | 0 | 24.2 | 2.22
4437 | 0 | 0 | 0 | 24.2 | 2.78
4438 | 0 | 0 | 0 | 23.7 | 3.89
4439 | 0 | 0 | 0 | 22.9 | 4.44
4440 | 0 | 0 | 0 | 22.2 | 1.39
4441 | 0 | 0 | 0 | 21.7 | 4.44
4442 | 0 | 0 | 0 | 21.2 | 3.33
4443 | 0 | 0 | 0 | 20.9 | 2.78
4444 | 0 | 0 | 0 | 20.3 | 3.89
4445 | 0 | 0 | 0 | 19.9 | 2.22
4446 | 47.2 | 47.2 | 0 | 20.2 | 1.67
4447 | 236.1 | 158.3 | 180.6 | 21.4 | 3.33
4448 | 488.9 | 294.4 | 306.8 | 23.1 | 3.89
4449 | 605.6 | 386.1 | 274.4 | 24.9 | 3.89
4450 | 688.9 | 486.1 | 221.1 | 25.8 | 5.56
4451 | 622.2 | 555.6 | 68.2 | 26.6 | 7.5
4452 | 580.6 | 547.2 | 34.1 | 27.6 | 6.67
4453 | 608.3 | 452.8 | 169.6 | 28.1 | 6.11
4454 | 480.6 | 352.8 | 159.8 | 29.1 | 7.22
4455 | 349.8 | 252.5 | 183.1 | 29.4 | 4.44
4456 | 189.9 | 154.4 | 157 | 28.5 | 5.56
4457 | 69.4 | 72.2 | 0 | 23.1 | 4.44
4458 | 2.8 | 0 | 0 | 24.4 | 2.78
4459 | 0 | 0 | 0 | 21.4 | 3.33
4460 | 0 | 0 | 0 | 21.6 | 7.22
4461 | 0 | 0 | 0 | 21.7 | 4.44
4462 | 0 | 0 | 0 | 21.6 | 4.44
4463 | 0 | 0 | 0 | 21.5 | 4.44
4464 | 0 | 0 | 0 | 21.16 | 1.67
4465 | 0 | 0 | 0 | 20.91 | 5
4466 | 0 | 0 | 0 | 20.63 | 3.89
4467 | 0 | 0 | 0 | 20.31 | 3.33
4468 | 0 | 0 | 0 | 20.08 | 3.89
4469 | 2.8 | 4.3 | 0 | 19.8 | 3.33
4470 | 63.9 | 77.7 | 236 | 19.9 | 3.89
4471 | 230.6 | 195.2 | 168.9 | 20.87 | 3.33
4472 | 375 | 294.6 | 240.4 | 22.37 | 3.89
4473 | 716.7 | 370 | 234.5 | 23.98 | 4.44
4474 | 841.7 | 308.3 | 581.5 | 25.4 | 4.44
4475 | 827.8 | 344.4 | 494.2 | 26.57 | 5.56
4476 | 627.7 | 316.7 | 245 | 27.69 | 5.56
4477 | 791.7 | 313.9 | 520.9 | 28.23 | 6.11
4478 | 438.9 | 308.3 | 163.2 | 28.37 | 5.56
4479 | 383.3 | 216.7 | 262.9 | 28.27 | 5.56
4480 | 150 | 136.1 | 32.3 | 27.55 | 6.67
4481 | 61.1 | 36.1 | 122.6 | 26.09 | 5
4482 | 11.1 | 0 | 0 | 28.1 | 4.44
4483 | 0 | 0 | 0 | 26 | 3.33
4484 | 0 | 0 | 0 | 23.4 | 6.11
4485 | 0 | 0 | 0 | 22.7 | 5
4486 | 0 | 0 | 0 | 22.9 | 3.33
4487 | 0 | 0 | 0 | 22.5 | 5
4488 | 0 | 0 | 0 | 21.6 | 1.94
4489 | 0 | 0 | 0 | 21.1 | 5.56
4490 | 0 | 0 | 0 | 20.5 | 5.56
4491 | 0 | 0 | 0 | 20 | 6.67
4492 | 0 | 0 | 0 | 19.5 | 4.44
4493 | 8.3 | 2.8 | 0 | 19 | 3.89
4494 | 172.2 | 91.7 | 395.6 | 19.3 | 3.89
4495 | 338.9 | 197.2 | 329.1 | 20.7 | 3.89
4496 | 463.9 | 302.8 | 254.2 | 21.7 | 5.56
4497 | 472.2 | 372.2 | 125 | 24 | 6.11
4498 | 450 | 463.9 | 0 | 25 | 7.78
4499 | 502.8 | 502.8 | 0 | 26 | 7.22
4500 | 627.7 | 418.6 | 245 | 27.5 | 6.67
4501 | 625.9 | 380 | 300.5 | 28.5 | 8.33
4502 | 504.5 | 328 | 282.3 | 28.3 | 7.78
4503 | 349.8 | 252.5 | 183.1 | 28.2 | 8.89
4504 | 127.8 | 125 | 6.5 | 27.4 | 7.22
4505 | 116.7 | 77.8 | 191 | 25.7 | 7.22
4506 | 2.8 | 0 | 0 | 24 | 6.94
4507 | 0 | 0 | 0 | 22.5 | 7.78
4508 | 0 | 0 | 0 | 22 | 5.56
4509 | 0 | 0 | 0 | 21.5 | 6.11
4510 | 0 | 0 | 0 | 21.4 | 5.56
4511 | 0 | 0 | 0 | 21 | 6.67
4512 | 0 | 0 | 0 | 20.7 | 2.22
4513 | 0 | 0 | 0 | 20.3 | 5
4514 | 0 | 0 | 0 | 20 | 3.89
4515 | 0 | 0 | 0 | 20 | 6.67
4516 | 0 | 0 | 0 | 19.9 | 4.72
4517 | 8.3 | 5.6 | 0 | 19.5 | 5.56
4518 | 127.8 | 94.4 | 163.9 | 19.5 | 5
4519 | 247.2 | 202.8 | 103.3 | 20.5 | 6.11
4520 | 411.1 | 336.1 | 118.3 | 21.9 | 6.67
4521 | 633.3 | 369.4 | 329.8 | 23.8 | 6.67
4522 | 622.2 | 441.7 | 196.7 | 25.7 | 6.67
4523 | 852.8 | 405.6 | 457 | 26.6 | 6.67
4524 | 863.9 | 433.3 | 440 | 27.4 | 6.67
4525 | 725 | 402.8 | 351.1 | 28 | 6.67
4526 | 572.2 | 341.7 | 288.1 | 28.8 | 6.67
4527 | 338.9 | 300 | 61.3 | 28.8 | 6.11
4528 | 175 | 188.9 | 0 | 28 | 5.56
4529 | 58.3 | 77.8 | 0 | 26.3 | 5.56
4530 | 0 | 2.8 | 0 | 25.3 | 5.56
4531 | 0 | 0 | 0 | 22.3 | 5.56
4532 | 0 | 0 | 0 | 21.3 | 5.56
4533 | 0 | 0 | 0 | 21.2 | 2.78
4534 | 0 | 0 | 0 | 21 | 3.89
4535 | 0 | 0 | 0 | 20.6 | 3.89
4536 | 0 | 0 | 0 | 20.3 | 2.5
4537 | 0 | 0 | 0 | 20 | 4.44
4538 | 0 | 0 | 0 | 19.8 | 3.89
4539 | 0 | 0 | 0 | 19.5 | 3.89
4540 | 0 | 0 | 0 | 19.3 | 3.89
4541 | 0 | 2.8 | 0 | 19.2 | 4.17
4542 | 63.9 | 72.2 | 0 | 19.1 | 5
4543 | 294.4 | 188.9 | 245.3 | 20.3 | 3.33
4544 | 508.3 | 300 | 328.6 | 21.8 | 5
4545 | 528.8 | 370 | 234.5 | 23.7 | 6.11
4546 | 618.9 | 404.4 | 274 | 25.3 | 5.56
4547 | 682.5 | 435.1 | 278.1 | 26.3 | 5.56
4548 | 788.9 | 388.9 | 408.6 | 27.7 | 5.56
4549 | 711.1 | 416.7 | 320.8 | 28.7 | 5.56
4550 | 504.5 | 328 | 282.3 | 29.6 | 5
4551 | 349.8 | 252.5 | 183.1 | 29.4 | 5.56
4552 | 194.4 | 177.8 | 38.7 | 29.1 | 5
4553 | 58.3 | 38.9 | 95.8 | 28 | 3.89
4554 | 2.8 | 0 | 0 | 26.8 | 5.56
4555 | 0 | 0 | 0 | 26.4 | 5.56
4556 | 0 | 0 | 0 | 25.1 | 5
4557 | 0 | 0 | 0 | 24.4 | 5
4558 | 0 | 0 | 0 | 22.8 | 3.33
4559 | 0 | 0 | 0 | 22.3 | 3.89
4560 | 0 | 0 | 0 | 21.16 | 2.78
4561 | 0 | 0 | 0 | 20.91 | 3.89
4562 | 0 | 0 | 0 | 20.63 | 3.33
4563 | 0 | 0 | 0 | 20.31 | 3.89
4564 | 0 | 0 | 0 | 20.08 | 4.44
4565 | 0 | 5.6 | 0 | 19.8 | 3.33
4566 | 94.4 | 75 | 95.9 | 19.9 | 3.33
4567 | 330.6 | 177.8 | 355.2 | 20.87 | 5
4568 | 508.3 | 261.1 | 389.9 | 22.37 | 5
4569 | 636.1 | 461.1 | 218.6 | 23.98 | 5.56
4570 | 669.4 | 447.2 | 242 | 25.4 | 5
4571 | 611.1 | 477.8 | 136.2 | 26.57 | 6.11
4572 | 697.2 | 466.7 | 235.4 | 27.69 | 5.56
4573 | 769.4 | 386.1 | 417.5 | 28.23 | 5.56
4574 | 758.3 | 308.3 | 562.1 | 28.37 | 3.89
4575 | 513.9 | 255.6 | 407.4 | 28.27 | 2.78
4576 | 286.1 | 188.9 | 226 | 27.55 | 2.78
4577 | 50 | 80.6 | 0 | 26.09 | 3.33
4578 | 0 | 13.9 | 0 | 27.4 | 3.33
4579 | 0 | 0 | 0 | 26.5 | 3.33
4580 | 0 | 0 | 0 | 25.5 | 3.89
4581 | 0 | 0 | 0 | 24.6 | 3.89
4582 | 0 | 0 | 0 | 23.5 | 2.78
4583 | 0 | 0 | 0 | 22.6 | 3.33
4584 | 0 | 0 | 0 | 21.6 | 3.06
4585 | 0 | 0 | 0 | 21.4 | 2.22
4586 | 0 | 0 | 0 | 21.1 | 3.06
4587 | 0 | 0 | 0 | 20.6 | 3.33
4588 | 0 | 0 | 0 | 20.1 | 3.89
4589 | 16.7 | 2.8 | 0 | 19.6 | 3.33
4590 | 155.6 | 83.3 | 357 | 19.7 | 4.44
4591 | 386.1 | 175 | 491 | 20.8 | 3.33
4592 | 561.1 | 200 | 569.5 | 22.9 | 3.89
4593 | 705.6 | 225 | 600.1 | 25.1 | 3.33
4594 | 802.8 | 236.1 | 616.9 | 26.5 | 5.56
4595 | 861.1 | 272.2 | 601.2 | 28.2 | 5.56
4596 | 752.8 | 363.9 | 397 | 29 | 5.56
4597 | 777.8 | 355.6 | 459.7 | 30.5 | 5
4598 | 527.8 | 319.4 | 260.2 | 30.4 | 5
4599 | 277.8 | 255.6 | 35 | 30.4 | 3.33
4600 | 233.3 | 180.6 | 122.8 | 30.1 | 3.33
4601 | 44.4 | 58.3 | 0 | 29.7 | 2.22
4602 | 0 | 0 | 0 | 28.2 | 2.78
4603 | 0 | 0 | 0 | 24.4 | 2.22
4604 | 0 | 0 | 0 | 23.7 | 5.56
4605 | 0 | 0 | 0 | 23.7 | 3.89
4606 | 0 | 0 | 0 | 23.7 | 2.78
4607 | 0 | 0 | 0 | 23.4 | 3.89
4608 | 0 | 0 | 0 | 22.7 | 3.33
4609 | 0 | 0 | 0 | 22.2 | 3.33
4610 | 0 | 0 | 0 | 21.7 | 2.78
4611 | 0 | 0 | 0 | 21.2 | 3.33
4612 | 0 | 0 | 0 | 21 | 2.78
4613 | 13.9 | 8.3 | 0 | 20.7 | 2.78
4614 | 122.2 | 94.4 | 137.6 | 20.8 | 3.89
4615 | 286.1 | 188.9 | 226.2 | 22.2 | 2.78
4616 | 422.2 | 325 | 153.3 | 23.3 | 4.44
4617 | 583.3 | 400 | 228.9 | 25.5 | 3.89
4618 | 844.4 | 358.3 | 529 | 27 | 3.33
4619 | 747.2 | 413.9 | 340.2 | 28.3 | 3.89
4620 | 500 | 363.9 | 138.9 | 29.1 | 2.22
4621 | 586.1 | 400 | 202.5 | 30.1 | 3.89
4622 | 477.8 | 330.6 | 183.8 | 30.5 | 3.89
4623 | 447.2 | 322.2 | 197.1 | 30.5 | 3.33
4624 | 172.2 | 194.4 | 0 | 29.3 | 3.33
4625 | 16.7 | 19.4 | 0 | 28 | 4.17
4626 | 0 | 0 | 0 | 22.9 | 3.89
4627 | 0 | 0 | 0 | 21.5 | 6.11
4628 | 0 | 0 | 0 | 21 | 5.56
4629 | 0 | 0 | 0 | 21 | 7.22
4630 | 0 | 0 | 0 | 20.7 | 7.78
4631 | 0 | 0 | 0 | 20.7 | 6.67
4632 | 0 | 0 | 0 | 20.9 | 3.61
4633 | 0 | 0 | 0 | 20.5 | 8.89
4634 | 0 | 0 | 0 | 20.2 | 8.33
4635 | 0 | 0 | 0 | 19.7 | 7.78
4636 | 0 | 0 | 0 | 19.5 | 7.22
4637 | 0 | 11.1 | 0 | 19.2 | 8.33
4638 | 66.7 | 150 | 0 | 19.1 | 7.22
4639 | 202.8 | 269.4 | 0 | 20.2 | 6.67
4640 | 494.4 | 427.8 | 105.1 | 21.7 | 7.22
4641 | 541.7 | 508.3 | 41.6 | 23.1 | 8.33
4642 | 622.2 | 508.3 | 123.9 | 24.1 | 7.22
4643 | 650 | 583.3 | 68 | 25.4 | 6.67
4644 | 547.2 | 527.8 | 19.8 | 27.1 | 7.22
4645 | 558.3 | 430.6 | 139 | 27.1 | 6.67
4646 | 552.8 | 447.2 | 131.8 | 26.5 | 6.11
4647 | 480.6 | 450 | 48.2 | 26.8 | 6.67
4648 | 233.3 | 154.4 | 157 | 26.5 | 6.67
4649 | 65.8 | 108.3 | 81.4 | 21.4 | 6.67
4650 | 2.4 | 16.7 | 0 | 21.1 | 7.22
4651 | 0 | 0 | 0 | 21.1 | 5.56
4652 | 0 | 0 | 0 | 21 | 5.56
4653 | 0 | 0 | 0 | 20.8 | 5
4654 | 0 | 0 | 0 | 20.4 | 4.44
4655 | 0 | 0 | 0 | 20.1 | 5
4656 | 0 | 0 | 0 | 19.9 | 3.89
4657 | 0 | 0 | 0 | 19.9 | 7.22
4658 | 0 | 0 | 0 | 20 | 5.56
4659 | 0 | 0 | 0 | 19.9 | 4.17
4660 | 0 | 0 | 0 | 19.4 | 5.56
4661 | 0 | 5.6 | 0 | 19.3 | 5
4662 | 96.7 | 80.6 | 236 | 19.4 | 4.44
4663 | 247.4 | 172.2 | 168.9 | 20.4 | 4.44
4664 | 417.6 | 255.6 | 240.4 | 20.2 | 6.67
4665 | 361.1 | 330.6 | 38.1 | 22.9 | 7.22
4666 | 527.8 | 458.3 | 75.5 | 25 | 6.67
4667 | 733.3 | 411.1 | 328.6 | 26.5 | 7.78
4668 | 736.1 | 405.6 | 337.1 | 27.7 | 7.78
4669 | 494.4 | 436.1 | 63.4 | 28.5 | 7.22
4670 | 322.2 | 227.8 | 117.9 | 27.5 | 8.33
4671 | 69.4 | 55.6 | 21.9 | 26.5 | 8.89
4672 | 19.4 | 154.4 | 157 | 24 | 9.44
4673 | 27.8 | 30.6 | 0 | 20.9 | 8.33
4674 | 0 | 5.6 | 0 | 20.5 | 8.89
4675 | 0 | 0 | 0 | 20.5 | 6.11
4676 | 0 | 0 | 0 | 20.5 | 5.56
4677 | 0 | 0 | 0 | 20.4 | 6.11
4678 | 0 | 0 | 0 | 20.4 | 5
4679 | 0 | 0 | 0 | 20.4 | 5
4680 | 0 | 0 | 0 | 21.16 | 4.17
4681 | 0 | 0 | 0 | 20.91 | 5
4682 | 0 | 0 | 0 | 20.63 | 4.17
4683 | 0 | 0 | 0 | 20.31 | 3.61
4684 | 0 | 0 | 0 | 20.08 | 3.89
4685 | 8.3 | 0 | 0 | 19.8 | 5.28
4686 | 180.6 | 77.7 | 236 | 19.9 | 4.72
4687 | 302.8 | 195.2 | 168.9 | 20.87 | 4.72
4688 | 336.1 | 308.3 | 43.8 | 22.37 | 5.83
4689 | 566.7 | 336.1 | 287.6 | 23.98 | 7.22
4690 | 663.9 | 450 | 232.5 | 25.4 | 6.94
4691 | 650 | 513.9 | 138.7 | 26.57 | 8.33
4692 | 566.7 | 458.3 | 110.4 | 27.69 | 7.78
4693 | 469.4 | 402.8 | 72.5 | 28.23 | 6.67
4694 | 444.4 | 302.8 | 176.7 | 28.37 | 7.5
4695 | 172.2 | 177.8 | 0 | 28.27 | 5.83
4696 | 127.8 | 155.6 | 0 | 27.55 | 4.44
4697 | 83.3 | 86.1 | 0 | 26.09 | 2.78
4698 | 2.8 | 2.8 | 0 | 24.95 | 2.78
4699 | 0 | 0 | 0 | 23.62 | 5
4700 | 0 | 0 | 0 | 22.89 | 5.56
4701 | 0 | 0 | 0 | 22.51 | 3.89
4702 | 0 | 0 | 0 | 22.05 | 5
4703 | 0 | 0 | 0 | 21.6 | 3.61
4704 | 0 | 0 | 0 | 20.7 | 4.44
4705 | 0 | 0 | 0 | 20.7 | 4.72
4706 | 0 | 0 | 0 | 20.6 | 4.17
4707 | 0 | 0 | 0 | 20.4 | 4.72
4708 | 0 | 0 | 0 | 20.4 | 3.61
4709 | 0 | 4.3 | 0 | 20.2 | 3.61
4710 | 38.9 | 77.7 | 236 | 20.3 | 4.44
4711 | 127.8 | 195.2 | 168.9 | 21.1 | 4.44
4712 | 166.7 | 294.6 | 240.4 | 22.4 | 4.17
4713 | 208.3 | 370 | 234.5 | 23 | 5
4714 | 419.4 | 404.4 | 274 | 24 | 6.11
4715 | 347.2 | 435.1 | 278.1 | 25.2 | 5.83
4716 | 344.4 | 418.6 | 245 | 26.6 | 5
4717 | 580.6 | 380 | 300.5 | 27 | 6.94
4718 | 425 | 328 | 282.3 | 27 | 7.22
4719 | 300 | 252.5 | 183.1 | 23.9 | 5.56
4720 | 163.9 | 154.4 | 157 | 24 | 5.56
4721 | 52.8 | 68.4 | 81.4 | 24 | 6.11
4722 | 2.8 | 4.2 | 0 | 23.2 | 6.39
4723 | 0 | 0 | 0 | 22.5 | 4.72
4724 | 0 | 0 | 0 | 21.8 | 5.28
4725 | 0 | 0 | 0 | 21.5 | 4.17
4726 | 0 | 0 | 0 | 21 | 5
4727 | 0 | 0 | 0 | 20.7 | 3.61
4728 | 0 | 0 | 0 | 20.7 | 4.72
4729 | 0 | 0 | 0 | 20.7 | 5
4730 | 0 | 0 | 0 | 20.5 | 5
4731 | 0 | 0 | 0 | 20.5 | 5
4732 | 0 | 0 | 0 | 20.5 | 5.56
4733 | 0 | 0 | 0 | 20.5 | 6.11
4734 | 47.2 | 55.6 | 0 | 20.6 | 5
4735 | 169.4 | 177.8 | 0 | 21.5 | 4.44
4736 | 363.9 | 333.3 | 48.2 | 22.5 | 5
4737 | 463.9 | 408.3 | 69.3 | 24.2 | 5.56
4738 | 616.7 | 550 | 72.4 | 26.5 | 6.67
4739 | 533.3 | 536.1 | 0 | 26.5 | 7.22
4740 | 511.1 | 522.2 | 0 | 27 | 6.67
4741 | 477.8 | 477.8 | 0 | 27 | 7.22
4742 | 405.6 | 408.3 | 0 | 27 | 8.89
4743 | 180.6 | 180.6 | 0 | 27 | 8.33
4744 | 155.6 | 152.8 | 6.5 | 26 | 8.33
4745 | 66.7 | 58.3 | 41.7 | 25 | 8.33
4746 | 8.3 | 0 | 0 | 24 | 8.33
4747 | 0 | 0 | 0 | 23.5 | 6.67
4748 | 0 | 0 | 0 | 22.5 | 7.22
4749 | 0 | 0 | 0 | 21.9 | 6.67
4750 | 0 | 0 | 0 | 21.5 | 6.67
4751 | 0 | 0 | 0 | 21.1 | 5.56
4752 | 0 | 0 | 0 | 21.1 | 5
4753 | 0 | 0 | 0 | 21 | 7.78
4754 | 0 | 0 | 0 | 20.9 | 7.78
4755 | 0 | 0 | 0 | 20.5 | 6.67
4756 | 0 | 0 | 0 | 20.4 | 6.67
4757 | 13.9 | 0 | 0 | 20.4 | 6.11
4758 | 136.1 | 52.8 | 418.4 | 20.5 | 5.56
4759 | 236.1 | 205.6 | 71.3 | 21.3 | 5
4760 | 411.1 | 325 | 135.8 | 22.6 | 6.11
4761 | 611.1 | 388.9 | 277 | 24.7 | 7.78
4762 | 658.3 | 450 | 226.2 | 26.3 | 10.56
4763 | 733.3 | 455.6 | 282.8 | 27.4 | 10
4764 | 644.4 | 422.2 | 226.2 | 28 | 9.44
4765 | 552.8 | 436.1 | 126.7 | 28.9 | 10
4766 | 575 | 436.1 | 173.1 | 27.9 | 10
4767 | 438.9 | 341.7 | 153.3 | 27.8 | 9.44
4768 | 222.2 | 211.1 | 25.9 | 27.1 | 8.33
4769 | 50 | 58.3 | 0 | 25.9 | 8.89
4770 | 2.8 | 2.8 | 0 | 24.5 | 8.89
4771 | 0 | 0 | 0 | 22.4 | 8.33
4772 | 0 | 0 | 0 | 21.9 | 6.67
4773 | 0 | 0 | 0 | 21.4 | 5
4774 | 0 | 0 | 0 | 20.9 | 4.44
4775 | 0 | 0 | 0 | 20.5 | 5
4776 | 0 | 0 | 0 | 20.1 | 5.28
4777 | 0 | 0 | 0 | 20 | 6.11
4778 | 0 | 0 | 0 | 19.8 | 6.11
4779 | 0 | 0 | 0 | 19.9 | 4.44
4780 | 0 | 0 | 0 | 19.9 | 5.56
4781 | 25 | 5.6 | 0 | 19.5 | 4.44
4782 | 158.3 | 105.6 | 265.7 | 19.7 | 5.56
4783 | 225 | 169.4 | 129.7 | 20.4 | 5
4784 | 394.4 | 277.8 | 183.9 | 22.1 | 5.56
4785 | 405.6 | 325 | 100.4 | 24.5 | 7.22
4786 | 422.2 | 400 | 24.1 | 24.4 | 8.33
4787 | 600 | 416.7 | 186.5 | 23.2 | 7.22
4788 | 527.8 | 416.7 | 113.1 | 26.7 | 7.78
4789 | 386.1 | 405.6 | 0 | 26.4 | 8.33
4790 | 500 | 388.9 | 138.5 | 28.2 | 7.22
4791 | 319.4 | 230.6 | 140.1 | 27.4 | 7.78
4792 | 119.4 | 113.9 | 13 | 25.2 | 7.78
4793 | 55.6 | 55.6 | 0 | 21.1 | 6.67
4794 | 8.3 | 0 | 0 | 20.6 | 6.67
4795 | 0 | 0 | 0 | 20.6 | 6.11
4796 | 0 | 0 | 0 | 20.6 | 5.56
4797 | 0 | 0 | 0 | 20.5 | 5.56
4798 | 0 | 0 | 0 | 20.6 | 3.89
4799 | 0 | 0 | 0 | 20.4 | 3.89
4800 | 0 | 0 | 0 | 20.3 | 5.56
4801 | 0 | 0 | 0 | 20.1 | 3.89
4802 | 0 | 0 | 0 | 20 | 6.11
4803 | 0 | 0 | 0 | 19.6 | 6.11
4804 | 0 | 0 | 0 | 19.6 | 3.89
4805 | 6.4 | 13.9 | 0 | 19.5 | 5
4806 | 96.7 | 69.4 | 236 | 19.6 | 4.44
4807 | 247.4 | 177.8 | 168.9 | 20.2 | 3.89
4808 | 417.6 | 275 | 240.4 | 22.7 | 3.89
4809 | 528.8 | 386.1 | 234.5 | 24.1 | 5.56
4810 | 483.3 | 425 | 63.3 | 25.1 | 6.67
4811 | 469.4 | 450 | 19.8 | 26.6 | 6.11
4812 | 538.9 | 372.2 | 169.5 | 27.8 | 5.56
4813 | 350 | 294.4 | 60.3 | 29.6 | 5
4814 | 277.8 | 283.3 | 0 | 27.6 | 5
4815 | 255.6 | 252.8 | 4.4 | 27.6 | 6.67
4816 | 250 | 77.8 | 402.3 | 24.4 | 5.56
4817 | 52.8 | 13.9 | 196.3 | 21.4 | 4.44
4818 | 2.8 | 0 | 0 | 21.8 | 3.89
4819 | 0 | 0 | 0 | 21.1 | 2.78
4820 | 0 | 0 | 0 | 20.7 | 3.89
4821 | 0 | 0 | 0 | 21 | 3.89
4822 | 0 | 0 | 0 | 20.7 | 5.56
4823 | 0 | 0 | 0 | 20.4 | 4.44
4824 | 0 | 0 | 0 | 20.1 | 5.83
4825 | 0 | 0 | 0 | 20.1 | 6.11
4826 | 0 | 0 | 0 | 20.1 | 5
4827 | 0 | 0 | 0 | 20 | 5
4828 | 0 | 0 | 0 | 20 | 5.56
4829 | 16.7 | 0 | 0 | 19.8 | 5
4830 | 75 | 30.6 | 225 | 19.7 | 5
4831 | 147.2 | 105.6 | 97.4 | 19.9 | 5
4832 | 286.1 | 230.6 | 87.6 | 20.9 | 5.56
4833 | 397.2 | 375 | 27.7 | 22.2 | 6.11
4834 | 291.7 | 322.2 | 0 | 24.5 | 7.22
4835 | 682.5 | 411.1 | 278.1 | 24.6 | 7.22
4836 | 250 | 288.9 | 0 | 25.5 | 7.22
4837 | 625.9 | 380 | 300.5 | 25.9 | 7.78
4838 | 504.5 | 328 | 282.3 | 25.5 | 7.78
4839 | 225 | 269.4 | 0 | 24.6 | 7.22
4840 | 38.9 | 47.2 | 0 | 24.7 | 7.22
4841 | 50 | 61.1 | 0 | 24.5 | 6.67
4842 | 0 | 0 | 0 | 23.2 | 6.11
4843 | 0 | 0 | 0 | 22.4 | 6.11
4844 | 0 | 0 | 0 | 21.8 | 5.56
4845 | 0 | 0 | 0 | 21 | 5.56
4846 | 0 | 0 | 0 | 20.3 | 4.44
4847 | 0 | 0 | 0 | 19.6 | 5
4848 | 0 | 0 | 0 | 19.6 | 6.11
4849 | 0 | 0 | 0 | 19.7 | 5.56
4850 | 0 | 0 | 0 | 19.6 | 7.22
4851 | 0 | 0 | 0 | 19.4 | 6.67
4852 | 0 | 0 | 0 | 19.3 | 6.67
4853 | 0 | 0 | 0 | 19.4 | 6.67
4854 | 58.3 | 94.4 | 0 | 19.5 | 5.56
4855 | 252.8 | 219.4 | 78 | 21.2 | 8.89
4856 | 441.7 | 322.2 | 188.3 | 21 | 7.22
4857 | 608.3 | 386.1 | 276.7 | 22.6 | 7.22
4858 | 675 | 386.1 | 313.2 | 24 | 6.67
4859 | 636.1 | 402.8 | 237.1 | 26.5 | 7.78
4860 | 450 | 433.3 | 16.9 | 27.5 | 8.33
4861 | 658.3 | 419.4 | 259 | 27.5 | 7.78
4862 | 505.6 | 377.8 | 159.1 | 27.6 | 8.33
4863 | 272.2 | 266.7 | 8.8 | 27.5 | 7.22
4864 | 150 | 141.7 | 19.5 | 25 | 7.78
4865 | 100 | 91.7 | 42.3 | 24.5 | 7.78
4866 | 2.8 | 8.3 | 0 | 24 | 6.11
4867 | 0 | 0 | 0 | 22.7 | 7.78
4868 | 0 | 0 | 0 | 22 | 6.67
4869 | 0 | 0 | 0 | 21.5 | 4.44
4870 | 0 | 0 | 0 | 21 | 5
4871 | 0 | 0 | 0 | 21 | 5
4872 | 0 | 0 | 0 | 20.2 | 6.39
4873 | 0 | 0 | 0 | 20.5 | 3.89
4874 | 0 | 0 | 0 | 20.2 | 4.44
4875 | 0 | 0 | 0 | 20 | 5
4876 | 0 | 0 | 0 | 19.9 | 4.44
4877 | 27.8 | 0 | 0 | 19.5 | 5
4878 | 150 | 88.9 | 311.2 | 19.6 | 5.56
4879 | 363.9 | 252.8 | 260.1 | 20.1 | 5.56
4880 | 469.4 | 344.4 | 197.1 | 21.4 | 6.11
4881 | 561.1 | 461.1 | 124.5 | 22.4 | 7.22
4882 | 544.4 | 433.3 | 120.4 | 24.4 | 6.67
4883 | 636.1 | 461.1 | 177.7 | 26 | 7.78
4884 | 502.8 | 427.8 | 76.2 | 26.4 | 8.33
4885 | 744.4 | 422.2 | 349.2 | 27.4 | 8.33
4886 | 494.4 | 402.8 | 114.1 | 28.4 | 7.78
4887 | 469.4 | 355.6 | 179.6 | 27.4 | 7.22
4888 | 288.9 | 197.2 | 214.6 | 26.8 | 7.22
4889 | 113.9 | 116.7 | 0 | 26.3 | 6.67
4890 | 5.6 | 13.9 | 0 | 24.2 | 6.11
4891 | 0 | 0 | 0 | 23.4 | 5.56
4892 | 0 | 0 | 0 | 22.9 | 4.44
4893 | 0 | 0 | 0 | 22.4 | 5
4894 | 0 | 0 | 0 | 21.6 | 6.11
4895 | 0 | 0 | 0 | 20.9 | 5.56
4896 | 0 | 0 | 0 | 20.4 | 6.67
4897 | 0 | 0 | 0 | 20.1 | 3.89
4898 | 0 | 0 | 0 | 19.9 | 4.44
4899 | 0 | 0 | 0 | 19.4 | 5
4900 | 0 | 0 | 0 | 19.1 | 3.89
4901 | 0 | 2.8 | 0 | 18.5 | 3.89
4902 | 100 | 61.1 | 198.7 | 18.6 | 3.33
4903 | 269.4 | 197.2 | 169.2 | 19.6 | 5.56
4904 | 330.6 | 294.4 | 56.9 | 21.6 | 5.56
4905 | 447.2 | 394.4 | 65.7 | 23.1 | 7.78
4906 | 569.4 | 411.1 | 171.5 | 24.4 | 8.33
4907 | 588.9 | 505.6 | 84.6 | 26.1 | 6.67
4908 | 452.8 | 441.7 | 11.3 | 26.4 | 8.33
4909 | 352.8 | 433.3 | 0 | 27 | 8.33
4910 | 288.9 | 358.3 | 0 | 26.7 | 6.67
4911 | 294.4 | 269.4 | 39.4 | 27.6 | 6.67
4912 | 136.1 | 141.7 | 0 | 27.3 | 7.78
4913 | 72.2 | 88.9 | 0 | 25.8 | 5.56
4914 | 0 | 13.9 | 0 | 24.5 | 6.11
4915 | 0 | 0 | 0 | 23.6 | 6.67
4916 | 0 | 0 | 0 | 22.8 | 5
4917 | 0 | 0 | 0 | 22.6 | 5
4918 | 0 | 0 | 0 | 22.1 | 5.56
4919 | 0 | 0 | 0 | 21.6 | 4.44
4920 | 0 | 0 | 0 | 20.8 | 6.94
4921 | 0 | 0 | 0 | 20.4 | 5
4922 | 0 | 0 | 0 | 20.1 | 5.56
4923 | 0 | 0 | 0 | 19.6 | 4.44
4924 | 0 | 0 | 0 | 19.1 | 3.89
4925 | 0 | 4.3 | 0 | 18.6 | 3.89
4926 | 96.7 | 77.7 | 236 | 18.7 | 3.89
4927 | 247.4 | 195.2 | 168.9 | 20 | 3.33
4928 | 417.6 | 294.6 | 240.4 | 22 | 5
4929 | 528.8 | 370 | 234.5 | 23.3 | 5.56
4930 | 618.9 | 404.4 | 274 | 25 | 5.56
4931 | 763.9 | 447.2 | 321.3 | 27 | 6.11
4932 | 772.2 | 475 | 301.6 | 28.4 | 7.22
4933 | 552.8 | 463.9 | 96.3 | 28.8 | 7.22
4934 | 675 | 347.2 | 407.9 | 29.3 | 6.11
4935 | 461.1 | 272.2 | 297.9 | 29.5 | 5.56
4936 | 325 | 194.4 | 306 | 29 | 5
4937 | 91.7 | 80.6 | 57 | 28.5 | 6.67
4938 | 2.8 | 0 | 0 | 26.6 | 4.44
4939 | 0 | 0 | 0 | 25.7 | 5.56
4940 | 0 | 0 | 0 | 24.5 | 6.67
4941 | 0 | 0 | 0 | 23.5 | 4.44
4942 | 0 | 0 | 0 | 22.7 | 5
4943 | 0 | 0 | 0 | 22.2 | 5
4944 | 0 | 0 | 0 | 22 | 7.22
4945 | 0 | 0 | 0 | 21.5 | 5.56
4946 | 0 | 0 | 0 | 21 | 4.44
4947 | 0 | 0 | 0 | 20.8 | 5.56
4948 | 0 | 0 | 0 | 20.4 | 3.89
4949 | 2.8 | 0 | 0 | 20.4 | 3.33
4950 | 69.4 | 41.7 | 142.9 | 20.2 | 3.33
4951 | 241.7 | 172.2 | 162.9 | 20.8 | 4.44
4952 | 344.4 | 277.8 | 105.1 | 22.6 | 5
4953 | 536.1 | 369.4 | 207.4 | 23.7 | 5.56
4954 | 727.8 | 458.3 | 291.7 | 25.7 | 5.56
4955 | 858.3 | 333.3 | 532.5 | 27.1 | 3.89
4956 | 830.6 | 308.3 | 529.7 | 28.3 | 5
4957 | 730.6 | 344.4 | 418 | 29.8 | 5.56
4958 | 622.2 | 302.8 | 397.4 | 29.5 | 5.56
4959 | 550 | 247.2 | 477.5 | 29.8 | 5
4960 | 283.3 | 161.1 | 286.7 | 27.7 | 5.56
4961 | 119.4 | 100 | 100 | 27.9 | 3.89
4962 | 0 | 11.1 | 0 | 26.9 | 3.89
4963 | 0 | 0 | 0 | 25.6 | 3.89
4964 | 0 | 0 | 0 | 24.3 | 4.44
4965 | 0 | 0 | 0 | 23.8 | 3.33
4966 | 0 | 0 | 0 | 23.3 | 3.89
4967 | 0 | 0 | 0 | 22.8 | 3.89
4968 | 0 | 0 | 0 | 22.3 | 7.5
4969 | 0 | 0 | 0 | 22 | 3.33
4970 | 0 | 0 | 0 | 20.9 | 3.33
4971 | 0 | 0 | 0 | 20.5 | 3.33
4972 | 0 | 0 | 0 | 20.2 | 2.78
4973 | 2.8 | 0 | 0 | 19.8 | 2.22
4974 | 94.4 | 44.4 | 258.1 | 19.6 | 1.67
4975 | 225 | 202.8 | 52.2 | 20.8 | 2.78
4976 | 519.4 | 347.2 | 271.6 | 23.4 | 3.89
4977 | 516.7 | 413.9 | 127.8 | 24.4 | 5
4978 | 575 | 500 | 81.2 | 26.2 | 5.56
4979 | 761.1 | 522.2 | 242.2 | 27.2 | 3.89
4980 | 844.4 | 477.8 | 371.8 | 28.7 | 5.56
4981 | 738.9 | 400 | 366.7 | 29.2 | 4.44
4982 | 555.6 | 338.9 | 269.5 | 29.4 | 3.89
4983 | 536.1 | 266.7 | 425 | 29.2 | 3.89
4984 | 352.8 | 163.9 | 443.5 | 29.7 | 4.44
4985 | 69.4 | 91.7 | 0 | 28.7 | 3.89
4986 | 0 | 0 | 0 | 26.7 | 5
4987 | 0 | 0 | 0 | 24.3 | 3.89
4988 | 0 | 0 | 0 | 23.7 | 2.22
4989 | 0 | 0 | 0 | 23.4 | 1.67
4990 | 0 | 0 | 0 | 23.2 | 2.22
4991 | 0 | 0 | 0 | 22.7 | 2.22
4992 | 0 | 0 | 0 | 22.2 | 7.78
4993 | 0 | 0 | 0 | 22.1 | 3.33
4994 | 0 | 0 | 0 | 21.9 | 3.33
4995 | 0 | 0 | 0 | 20.8 | 2.78
4996 | 0 | 0 | 0 | 20.6 | 3.33
4997 | 0 | 16.7 | 0 | 20.2 | 3.33
4998 | 41.7 | 77.8 | 0 | 20.2 | 3.89
4999 | 169.4 | 169.4 | 0 | 20.7 | 2.78
5000 | 508.3 | 202.8 | 482 | 22.7 | 3.33
5001 | 627.8 | 313.9 | 390.4 | 24.6 | 3.89
5002 | 750 | 277.8 | 510.8 | 26.1 | 3.89
5003 | 841.7 | 288.9 | 560.2 | 27.3 | 4.17
5004 | 844.4 | 369.4 | 481.4 | 28.6 | 3.89
5005 | 769.4 | 405.6 | 393.6 | 29.1 | 3.89
5006 | 450 | 388.9 | 76 | 29.4 | 5
5007 | 294.4 | 219.4 | 118.3 | 29.1 | 4.44
5008 | 86.1 | 97.2 | 0 | 29.1 | 3.89
5009 | 58.3 | 66.7 | 0 | 27.4 | 3.33
5010 | 0 | 0 | 0 | 26.6 | 3.33
5011 | 0 | 0 | 0 | 25.6 | 1.67
5012 | 0 | 0 | 0 | 24.5 | 1.67
5013 | 0 | 0 | 0 | 24.4 | 2.22
5014 | 0 | 0 | 0 | 23.6 | 4.44
5015 | 0 | 0 | 0 | 22.7 | 5
5016 | 0 | 0 | 0 | 22.1 | 8.06
5017 | 0 | 0 | 0 | 21.3 | 3.89
5018 | 0 | 0 | 0 | 20.8 | 3.89
5019 | 0 | 0 | 0 | 20.3 | 4.44
5020 | 0 | 0 | 0 | 20.1 | 2.78
5021 | 0 | 0 | 0 | 19.6 | 3.33
5022 | 136.1 | 72.2 | 332.2 | 19.7 | 3.89
5023 | 225 | 216.7 | 19.6 | 20.6 | 3.33
5024 | 544.4 | 236.1 | 486.4 | 22.7 | 3.33
5025 | 597.2 | 297.2 | 373 | 24.7 | 3.33
5026 | 630.6 | 313.9 | 342.4 | 25.7 | 3.89
5027 | 619.4 | 383.3 | 239.2 | 27 | 2.78
5028 | 772.2 | 311.1 | 467.1 | 28 | 3.33
5029 | 705.6 | 225 | 519.6 | 29.1 | 2.78
5030 | 780.6 | 208.3 | 711.5 | 29.7 | 3.33
5031 | 513.9 | 188.9 | 512.7 | 29.4 | 1.67
5032 | 158.3 | 144.4 | 32.7 | 29.2 | 2.78
5033 | 38.9 | 44.4 | 0 | 27.7 | 1.67
5034 | 0 | 0 | 0 | 26.2 | 2.78
5035 | 0 | 0 | 0 | 23.2 | 2.78
5036 | 0 | 0 | 0 | 22.7 | 1.67
5037 | 0 | 0 | 0 | 22.9 | 1.67
5038 | 0 | 0 | 0 | 22.2 | 3.33
5039 | 0 | 0 | 0 | 21.5 | 3.89
5040 | 0 | 0 | 0 | 20.8 | 8.33
5041 | 0 | 0 | 0 | 20.3 | 3.89
5042 | 0 | 0 | 0 | 20.2 | 3.89
5043 | 0 | 0 | 0 | 20.2 | 3.33
5044 | 0 | 0 | 0 | 20.2 | 3.89
5045 | 0 | 5.6 | 0 | 20.1 | 3.89
5046 | 63.9 | 86.1 | 0 | 20.2 | 3.33
5047 | 325 | 252.8 | 170 | 20.7 | 1.67
5048 | 336.1 | 341.7 | 0 | 22.4 | 2.22
5049 | 375 | 408.3 | 0 | 23.3 | 2.78
5050 | 525 | 491.7 | 36 | 23.6 | 3.33
5051 | 713.9 | 611.1 | 104.1 | 24.9 | 3.33
5052 | 633.3 | 527.8 | 106.9 | 26 | 3.33
5053 | 858.3 | 202.8 | 708.6 | 26.9 | 3.33
5054 | 680.6 | 211.1 | 583.6 | 27.9 | 1.67
5055 | 488.9 | 191.7 | 469 | 29.1 | 2.22
5056 | 369.4 | 161.1 | 490.5 | 28.9 | 2.78
5057 | 127.8 | 102.8 | 130.5 | 28.4 | 2.78
5058 | 2.8 | 2.8 | 0 | 27.3 | 2.78
5059 | 0 | 0 | 0 | 26.4 | 1.67
5060 | 0 | 0 | 0 | 25.4 | 0.56
5061 | 0 | 0 | 0 | 23.6 | 4.44
5062 | 0 | 0 | 0 | 22.7 | 2.78
5063 | 0 | 0 | 0 | 21.9 | 2.78
5064 | 0 | 0 | 0 | 21.16 | 8.61
5065 | 0 | 0 | 0 | 20.91 | 2.78
5066 | 0 | 0 | 0 | 20.63 | 3.33
5067 | 0 | 0 | 0 | 20.31 | 3.33
5068 | 0 | 0 | 0 | 20.08 | 3.33
5069 | 0 | 4.3 | 0 | 19.8 | 2.78
5070 | 16.7 | 77.7 | 236 | 19.9 | 2.78
5071 | 41.7 | 195.2 | 168.9 | 20.87 | 3.33
5072 | 105.6 | 294.6 | 240.4 | 22.37 | 2.78
5073 | 200 | 370 | 234.5 | 23.98 | 2.78
5074 | 355.6 | 404.4 | 274 | 25.4 | 5.77
5075 | 580.6 | 435.1 | 278.1 | 26.57 | 2.78
5076 | 491.7 | 418.6 | 245 | 27.69 | 3.33
5077 | 494.4 | 380 | 300.5 | 28.23 | 3.33
5078 | 291.7 | 328 | 282.3 | 28.37 | 3.89
5079 | 194.4 | 252.5 | 183.1 | 28.27 | 2.78
5080 | 94.4 | 154.4 | 157 | 27.55 | 3.33
5081 | 13.9 | 68.4 | 81.4 | 26.09 | 2.78
5082 | 0 | 4.2 | 0 | 21.2 | 2.22
5083 | 0 | 0 | 0 | 21.7 | 1.67
5084 | 0 | 0 | 0 | 21.6 | 0
5085 | 0 | 0 | 0 | 21.6 | 1.67
5086 | 0 | 0 | 0 | 20.7 | 2.78
5087 | 0 | 0 | 0 | 20.1 | 3.89
5088 | 0 | 0 | 0 | 19.9 | 0.28
5089 | 0 | 0 | 0 | 20 | 2.78
5090 | 0 | 0 | 0 | 20.2 | 3.89
5091 | 0 | 0 | 0 | 20.4 | 3.89
5092 | 0 | 0 | 0 | 20.4 | 2.78
5093 | 0 | 0 | 0 | 20.6 | 2.78
5094 | 47.2 | 58.3 | 0 | 20.8 | 3.33
5095 | 216.7 | 216.7 | 0 | 21.5 | 3.89
5096 | 288.9 | 316.7 | 0 | 21.7 | 2.78
5097 | 444.4 | 433.3 | 13.8 | 23.1 | 3.33
5098 | 518 | 350 | 235.7 | 23.6 | 3.33
5099 | 150 | 138.9 | 11.2 | 25.6 | 3.33
5100 | 194.4 | 216.7 | 0 | 25.8 | 3.89
5101 | 380.6 | 422.2 | 0 | 25.1 | 5
5102 | 388.9 | 422.2 | 0 | 25.6 | 2.78
5103 | 288.9 | 311.1 | 0 | 26.1 | 2.78
5104 | 150 | 180.6 | 0 | 26 | 3.33
5105 | 136.1 | 108.3 | 146.2 | 23.4 | 2.22
5106 | 5.6 | 8.3 | 0 | 22.6 | 3.33
5107 | 0 | 0 | 0 | 22.1 | 2.78
5108 | 0 | 0 | 0 | 22.1 | 1.67
5109 | 0 | 0 | 0 | 21.4 | 1.67
5110 | 0 | 0 | 0 | 22.1 | 3.33
5111 | 0 | 0 | 0 | 20.7 | 3.89
5112 | 0 | 0 | 0 | 20.7 | 0.56
5113 | 0 | 0 | 0 | 20.4 | 3.89
5114 | 0 | 0 | 0 | 20.1 | 3.89
5115 | 0 | 0 | 0 | 20 | 5
5116 | 0 | 0 | 0 | 19.8 | 5
5117 | 0 | 2.8 | 0 | 19.6 | 3.89
5118 | 47.2 | 66.7 | 0 | 19.6 | 3.89
5119 | 197.2 | 186.1 | 26.2 | 20.1 | 3.89
5120 | 286.1 | 269.4 | 26.3 | 21.4 | 3.89
5121 | 286.1 | 291.7 | 0 | 23.4 | 5
5122 | 361.1 | 372.2 | 0 | 25 | 5
5123 | 519.4 | 421 | 255.5 | 24.4 | 5
5124 | 802.8 | 547.2 | 258.5 | 25.9 | 5
5125 | 666.7 | 411.1 | 276 | 27.4 | 4.44
5126 | 683.3 | 317.1 | 278.5 | 27.4 | 4.44
5127 | 427.8 | 238.8 | 289.7 | 27.5 | 3.33
5128 | 177.8 | 202.8 | 0 | 26.6 | 3.33
5129 | 88.9 | 75 | 73.4 | 26.6 | 2.78
5130 | 2.8 | 0 | 0 | 25.9 | 2.78
5131 | 0 | 0 | 0 | 25.4 | 2.78
5132 | 0 | 0 | 0 | 22.9 | 2.22
5133 | 0 | 0 | 0 | 21.7 | 5
5134 | 0 | 0 | 0 | 20.4 | 5
5135 | 0 | 0 | 0 | 20 | 4.44
5136 | 0 | 0 | 0 | 19.9 | 0.83
5137 | 0 | 0 | 0 | 19.9 | 5
5138 | 0 | 0 | 0 | 19.8 | 4.44
5139 | 0 | 0 | 0 | 19.5 | 3.89
5140 | 0 | 0 | 0 | 19.5 | 3.89
5141 | 0 | 0 | 0 | 19.4 | 4.44
5142 | 8.3 | 16.7 | 0 | 19.5 | 2.78
5143 | 52.8 | 63.9 | 0 | 19.8 | 2.22
5144 | 100 | 119.4 | 0 | 20 | 2.78
5145 | 216.7 | 236.1 | 0 | 20.1 | 3.33
5146 | 433.3 | 425 | 9 | 21 | 3.89
5147 | 572.2 | 533.3 | 39.3 | 23.6 | 3.89
5148 | 708.3 | 561.1 | 148.8 | 25.4 | 5
5149 | 800 | 450 | 377.9 | 26.6 | 5.56
5150 | 700 | 317.1 | 278.5 | 26.4 | 5
5151 | 408.3 | 238.8 | 289.7 | 26.5 | 5
5152 | 194.4 | 211.1 | 0 | 26.2 | 4.44
5153 | 69.4 | 52.8 | 88.5 | 23.6 | 3.33
5154 | 2.8 | 0 | 0 | 21 | 3.33
5155 | 0 | 0 | 0 | 21 | 5.56
5156 | 0 | 0 | 0 | 21.3 | 3.89
5157 | 0 | 0 | 0 | 21.2 | 3.33
5158 | 0 | 0 | 0 | 20.9 | 2.78
5159 | 0 | 0 | 0 | 20.2 | 3.89
5160 | 0 | 0 | 0 | 20.1 | 1.11
5161 | 0 | 0 | 0 | 19.8 | 5
5162 | 0 | 0 | 0 | 19.8 | 3.33
5163 | 0 | 0 | 0 | 19.7 | 3.89
5164 | 0 | 0 | 0 | 19.5 | 3.33
5165 | 0 | 1.2 | 0 | 19.8 | 3.89
5166 | 147.2 | 48.5 | 181.6 | 20.5 | 3.89
5167 | 255.6 | 147.5 | 188.7 | 21.7 | 4.44
5168 | 361.1 | 236.9 | 275.2 | 23.2 | 5.56
5169 | 361.1 | 317.8 | 294 | 23.9 | 5
5170 | 344.4 | 366.3 | 235.7 | 24.2 | 5.56
5171 | 366.7 | 421 | 255.5 | 24.7 | 6.67
5172 | 525 | 421.8 | 235.3 | 24.8 | 6.11
5173 | 547.2 | 388.2 | 262.2 | 24.9 | 6.11
5174 | 366.7 | 317.1 | 278.5 | 24.8 | 3.33
5175 | 88.9 | 238.8 | 289.7 | 20.5 | 5.56
5176 | 41.7 | 154.1 | 292.6 | 19.4 | 7.22
5177 | 52.8 | 58 | 217.8 | 19.3 | 3.89
5178 | 0 | 1.3 | 0 | 19.2 | 5
5179 | 0 | 0 | 0 | 19.7 | 5.56
5180 | 0 | 0 | 0 | 20 | 5.56
5181 | 0 | 0 | 0 | 19.8 | 6.67
5182 | 0 | 0 | 0 | 19.7 | 6.11
5183 | 0 | 0 | 0 | 19.5 | 7.78
5184 | 0 | 0 | 0 | 19.4 | 1.39
5185 | 0 | 0 | 0 | 19.4 | 7.22
5186 | 0 | 0 | 0 | 19.3 | 6.11
5187 | 0 | 0 | 0 | 19.3 | 5.56
5188 | 0 | 0 | 0 | 19.2 | 7.22
5189 | 0 | 0 | 0 | 19.1 | 7.22
5190 | 22.2 | 19.4 | 14.9 | 19 | 6.11
5191 | 119.4 | 130.6 | 0 | 19.3 | 7.22
5192 | 300 | 319.4 | 0 | 20.8 | 5.56
5193 | 411.1 | 391.7 | 24.2 | 22.3 | 6.11
5194 | 361.1 | 350 | 12 | 22.8 | 6.67
5195 | 675 | 494.4 | 182.4 | 24.3 | 5.56
5196 | 713.9 | 475 | 241.4 | 25.3 | 7.22
5197 | 419.4 | 433.3 | 0 | 25.5 | 7.22
5198 | 313.9 | 275 | 48.3 | 24.3 | 5.56
5199 | 319.4 | 247.2 | 114.1 | 21.9 | 5.56
5200 | 225 | 183.3 | 98.8 | 23.8 | 3.33
5201 | 63.9 | 69.4 | 0 | 21.8 | 2.78
5202 | 0 | 0 | 0 | 21.8 | 5.56
5203 | 0 | 0 | 0 | 20.9 | 5.56
5204 | 0 | 0 | 0 | 20.8 | 3.33
5205 | 0 | 0 | 0 | 20.8 | 5
5206 | 0 | 0 | 0 | 20.4 | 5.56
5207 | 0 | 0 | 0 | 20.3 | 4.17
5208 | 0 | 0 | 0 | 20.3 | 1.67
5209 | 0 | 0 | 0 | 20.3 | 5.28
5210 | 0 | 0 | 0 | 20.3 | 6.11
5211 | 0 | 0 | 0 | 20.3 | 5.56
5212 | 0 | 0 | 0 | 20.3 | 5.56
5213 | 0 | 0 | 0 | 20.1 | 6.11
5214 | 69.4 | 25 | 239.2 | 20.1 | 5.83
5215 | 144.4 | 125 | 46.1 | 20.7 | 5.56
5216 | 413.9 | 216.7 | 311.8 | 20.5 | 6.11
5217 | 483.3 | 402.8 | 100.1 | 22.4 | 6.11
5218 | 469.4 | 383.3 | 92.9 | 23.5 | 6.67
5219 | 602.8 | 469.4 | 134.7 | 23.7 | 7.22
5220 | 511.1 | 438.9 | 72.9 | 23.7 | 7.22
5221 | 497.2 | 405.6 | 98.9 | 22.2 | 8.89
5222 | 322.2 | 286.1 | 44.9 | 23.7 | 7.22
5223 | 247.2 | 233.3 | 22 | 23.2 | 8.33
5224 | 191.7 | 169.4 | 52.7 | 23.2 | 7.78
5225 | 75 | 55.6 | 104.6 | 22.6 | 7.22
5226 | 2.8 | 0 | 0 | 21.7 | 6.67
5227 | 0 | 0 | 0 | 21.1 | 6.67
5228 | 0 | 0 | 0 | 20.7 | 8.33
5229 | 0 | 0 | 0 | 20.2 | 7.22
5230 | 0 | 0 | 0 | 19.8 | 5.56
5231 | 0 | 0 | 0 | 19.7 | 6.11
5232 | 0 | 0 | 0 | 19.7 | 1.94
5233 | 0 | 0 | 0 | 19.6 | 5.56
5234 | 0 | 0 | 0 | 19.6 | 4.44
5235 | 0 | 0 | 0 | 19.5 | 5
5236 | 0 | 0 | 0 | 19.3 | 6.11
5237 | 0 | 2.8 | 0 | 19.3 | 6.67
5238 | 27.8 | 52.8 | 0 | 19.1 | 5.56
5239 | 63.9 | 58.3 | 13.2 | 19.3 | 5.56
5240 | 97.2 | 130.6 | 0 | 20.4 | 5.56
5241 | 188.9 | 225 | 0 | 20.9 | 6.67
5242 | 291.7 | 280.6 | 12 | 22.4 | 6.67
5243 | 408.3 | 444.4 | 0 | 24 | 8.33
5244 | 283.3 | 311.1 | 0 | 21.4 | 7.78
5245 | 472.2 | 463.9 | 9 | 23.2 | 6.67
5246 | 369.4 | 363.9 | 6.9 | 22.9 | 8.33
5247 | 194.4 | 208.3 | 0 | 23.1 | 6.11
5248 | 100 | 116.7 | 0 | 22 | 5.56
5249 | 41.7 | 44.4 | 0 | 21.1 | 7.22
5250 | 2.8 | 11.1 | 0 | 20.5 | 5
5251 | 0 | 0 | 0 | 20.1 | 7.22
5252 | 0 | 0 | 0 | 20 | 6.67
5253 | 0 | 0 | 0 | 19.9 | 6.67
5254 | 0 | 0 | 0 | 19.8 | 5.56
5255 | 0 | 0 | 0 | 19.7 | 5
5256 | 0 | 0 | 0 | 19.5 | 2.22
5257 | 0 | 0 | 0 | 19.5 | 8.33
5258 | 0 | 0 | 0 | 19.5 | 7.22
5259 | 0 | 0 | 0 | 19.4 | 6.11
5260 | 0 | 0 | 0 | 19.4 | 5
5261 | 0 | 0 | 0 | 19.3 | 6.11
5262 | 55.6 | 36.1 | 105.7 | 19.1 | 5.56
5263 | 238.9 | 141.7 | 231.3 | 19.4 | 6.11
5264 | 202.8 | 230.6 | 0 | 20.3 | 6.11
5265 | 325 | 283.3 | 51.8 | 20.8 | 6.11
5266 | 536.1 | 391.7 | 155.8 | 22.8 | 7.22
5267 | 666.7 | 477.8 | 190.7 | 24.6 | 7.22
5268 | 663.9 | 463.9 | 201.9 | 24.1 | 7.22
5269 | 447.2 | 363.9 | 89.9 | 25.3 | 9.17
5270 | 300 | 313.9 | 0 | 25.1 | 7.78
5271 | 363.2 | 430.6 | 289.7 | 23.1 | 7.78
5272 | 221.1 | 102.8 | 292.6 | 24.1 | 7.78
5273 | 78.7 | 52.8 | 217.8 | 24.1 | 5.56
5274 | 1.9 | 0 | 0 | 21.8 | 7.78
5275 | 0 | 0 | 0 | 20.9 | 11.11
5276 | 0 | 0 | 0 | 20.8 | 5.56
5277 | 0 | 0 | 0 | 20.9 | 5
5278 | 0 | 0 | 0 | 20.1 | 6.11
5279 | 0 | 0 | 0 | 19.9 | 6.11
5280 | 0 | 0 | 0 | 19.8 | 2.5
5281 | 0 | 0 | 0 | 19.7 | 5
5282 | 0 | 0 | 0 | 19.6 | 6.11
5283 | 0 | 0 | 0 | 19.7 | 5
5284 | 0 | 0 | 0 | 19.8 | 5
5285 | 0 | 0 | 0 | 19.6 | 6.11
5286 | 44.4 | 13.9 | 166.9 | 19.6 | 6.67
5287 | 130.6 | 147.5 | 188.7 | 19.8 | 6.67
5288 | 225 | 236.9 | 275.2 | 19.9 | 6.67
5289 | 308.3 | 317.8 | 294 | 21.9 | 8.33
5290 | 518 | 466.7 | 235.7 | 23.1 | 8.89
5291 | 397.2 | 413.9 | 0 | 24.7 | 6.11
5292 | 366.7 | 421.8 | 235.3 | 24.6 | 11.11
5293 | 311.1 | 355.6 | 0 | 24.6 | 7.22
5294 | 297.2 | 316.7 | 0 | 24.6 | 7.78
5295 | 363.2 | 238.8 | 289.7 | 23.5 | 6.11
5296 | 221.1 | 154.1 | 292.6 | 22 | 6.67
5297 | 50 | 41.7 | 45.5 | 21.6 | 6.67
5298 | 8.3 | 2.8 | 0 | 20.9 | 5.56
5299 | 0 | 0 | 0 | 20.6 | 5
5300 | 0 | 0 | 0 | 20.5 | 6.11
5301 | 0 | 0 | 0 | 20.6 | 3.33
5302 | 0 | 0 | 0 | 20.3 | 5
5303 | 0 | 0 | 0 | 20.1 | 6.11
5304 | 0 | 0 | 0 | 20.3 | 2.78
5305 | 0 | 0 | 0 | 20.3 | 5
5306 | 0 | 0 | 0 | 20.2 | 5.56
5307 | 0 | 0 | 0 | 20.1 | 4.44
5308 | 0 | 0 | 0 | 20.1 | 4.17
5309 | 0 | 5.6 | 0 | 20 | 4.44
5310 | 44.4 | 55.6 | 0 | 20 | 3.89
5311 | 161.1 | 166.7 | 0 | 20.2 | 5.28
5312 | 200 | 208.3 | 0 | 21.6 | 4.44
5313 | 375 | 369.4 | 6.9 | 22.7 | 5.28
5314 | 327.8 | 391.7 | 0 | 23.7 | 5
5315 | 336.1 | 363.9 | 0 | 24.2 | 4.72
5316 | 425 | 394.4 | 30.8 | 24.8 | 4.17
5317 | 400 | 363.9 | 38.9 | 21.8 | 4.44
5318 | 386.1 | 377.8 | 10.4 | 23 | 4.72
5319 | 202.8 | 202.8 | 0 | 24.2 | 5.56
5320 | 97.2 | 113.9 | 0 | 24.5 | 4.72
5321 | 16.7 | 36.1 | 0 | 24 | 5.83
5322 | 0 | 0 | 0 | 23.2 | 5.28
5323 | 0 | 0 | 0 | 22.7 | 5.83
5324 | 0 | 0 | 0 | 22 | 5
5325 | 0 | 0 | 0 | 21.2 | 4.17
5326 | 0 | 0 | 0 | 21 | 4.17
5327 | 0 | 0 | 0 | 20.6 | 5
5328 | 0 | 0 | 0 | 20.6 | 3.06
5329 | 0 | 0 | 0 | 20.4 | 5.28
5330 | 0 | 0 | 0 | 19.9 | 5
5331 | 0 | 0 | 0 | 19.7 | 3.61
5332 | 0 | 0 | 0 | 19.7 | 3.06
5333 | 0 | 1.2 | 0 | 19.7 | 3.61
5334 | 25 | 48.5 | 181.6 | 19.7 | 2.78
5335 | 186.1 | 147.5 | 188.7 | 20.3 | 3.33
5336 | 225 | 236.9 | 275.2 | 21.4 | 5.56
5337 | 325 | 317.8 | 294 | 22.9 | 5
5338 | 283.3 | 366.3 | 235.7 | 24 | 3.89
5339 | 191.7 | 421 | 255.5 | 24.3 | 5
5340 | 130.6 | 421.8 | 235.3 | 24 | 5.56
5341 | 177.8 | 388.2 | 262.2 | 24.6 | 5.56
5342 | 233.3 | 317.1 | 278.5 | 24.4 | 5.28
5343 | 277.8 | 238.8 | 289.7 | 23.9 | 4.44
5344 | 180.6 | 154.1 | 292.6 | 24.1 | 4.44
5345 | 41.7 | 58 | 217.8 | 24.94 | 5.83
5346 | 2.8 | 1.3 | 0 | 24.22 | 5.56
5347 | 0 | 0 | 0 | 23.41 | 4.44
5348 | 0 | 0 | 0 | 22.89 | 5
5349 | 0 | 0 | 0 | 22.42 | 4.44
5350 | 0 | 0 | 0 | 21 | 4.72
5351 | 0 | 0 | 0 | 20.6 | 5
5352 | 0 | 0 | 0 | 20.5 | 3.33
5353 | 0 | 0 | 0 | 20.4 | 4.44
5354 | 0 | 0 | 0 | 20.4 | 5
5355 | 0 | 0 | 0 | 20 | 4.72
5356 | 0 | 0 | 0 | 20.2 | 4.17
5357 | 0 | 1.2 | 0 | 19.9 | 4.44
5358 | 5.6 | 48.5 | 181.6 | 20 | 3.61
5359 | 94.4 | 147.5 | 188.7 | 20.4 | 3.33
5360 | 144.4 | 236.9 | 275.2 | 21.2 | 5.56
5361 | 83.3 | 317.8 | 294 | 21.3 | 6.67
5362 | 211.1 | 366.3 | 235.7 | 22.3 | 6.67
5363 | 347.2 | 421 | 255.5 | 23.2 | 6.11
5364 | 369.4 | 421.8 | 235.3 | 24.2 | 5.56
5365 | 266.7 | 388.2 | 262.2 | 24.3 | 6.11
5366 | 255.6 | 317.1 | 278.5 | 23.8 | 5
5367 | 219.4 | 238.8 | 289.7 | 22.7 | 2.22
5368 | 136.1 | 154.1 | 292.6 | 22.2 | 5.56
5369 | 25 | 58 | 217.8 | 22.4 | 5.56
5370 | 0 | 1.3 | 0 | 21.7 | 5
5371 | 0 | 0 | 0 | 21.7 | 5.56
5372 | 0 | 0 | 0 | 21.3 | 5
5373 | 0 | 0 | 0 | 21.2 | 6.11
5374 | 0 | 0 | 0 | 20.9 | 5
5375 | 0 | 0 | 0 | 20.7 | 5
5376 | 0 | 0 | 0 | 20.6 | 3.61
5377 | 0 | 0 | 0 | 20.4 | 5
5378 | 0 | 0 | 0 | 19.7 | 4.44
5379 | 0 | 0 | 0 | 19.7 | 4.44
5380 | 0 | 0 | 0 | 19.7 | 3.89
5381 | 0 | 1.2 | 0 | 19.7 | 3.89
5382 | 16.7 | 48.5 | 181.6 | 19.7 | 4.44
5383 | 69.4 | 147.5 | 188.7 | 19.7 | 5
5384 | 230.6 | 236.9 | 275.2 | 20.2 | 6.11
5385 | 177.8 | 317.8 | 294 | 22.1 | 7.22
5386 | 230.6 | 366.3 | 235.7 | 21.6 | 7.78
5387 | 247.2 | 421 | 255.5 | 22 | 5
5388 | 277.8 | 421.8 | 235.3 | 23.9 | 7.22
5389 | 222.2 | 388.2 | 262.2 | 24.1 | 7.78
5390 | 297.2 | 317.1 | 278.5 | 23.9 | 10
5391 | 250 | 238.8 | 289.7 | 23 | 7.22
5392 | 111.1 | 154.1 | 292.6 | 22.5 | 5.56
5393 | 5.6 | 58 | 217.8 | 22.1 | 7.22
5394 | 0 | 1.3 | 0 | 21.5 | 4.44
5395 | 0 | 0 | 0 | 21.1 | 3.89
5396 | 0 | 0 | 0 | 21.1 | 3.33
5397 | 0 | 0 | 0 | 20.6 | 3.89
5398 | 0 | 0 | 0 | 20.6 | 3.33
5399 | 0 | 0 | 0 | 20.3 | 4.44
5400 | 0 | 0 | 0 | 20.1 | 3.89
5401 | 0 | 0 | 0 | 20.1 | 3.33
5402 | 0 | 0 | 0 | 20.1 | 4.44
5403 | 0 | 0 | 0 | 20.1 | 4.44
5404 | 0 | 0 | 0 | 19.6 | 4.44
5405 | 0 | 0 | 0 | 19.4 | 3.89
5406 | 44.4 | 22.2 | 124.8 | 19.6 | 3.89
5407 | 152.8 | 116.7 | 86.7 | 20.2 | 2.78
5408 | 316.7 | 225 | 145.5 | 21.9 | 3.33
5409 | 494.4 | 408.3 | 107 | 23.3 | 3.33
5410 | 433.3 | 405.6 | 29.9 | 23.7 | 5.56
5411 | 419.4 | 325 | 95.2 | 24.8 | 6.11
5412 | 363.9 | 366.7 | 0 | 25.8 | 6.11
5413 | 425 | 350 | 80.8 | 25.8 | 4.44
5414 | 491.7 | 358.3 | 165.7 | 26.3 | 4.44
5415 | 422.2 | 255.6 | 264.5 | 25.8 | 4.44
5416 | 175 | 138.9 | 86.7 | 24.3 | 4.44
5417 | 38.9 | 50 | 0 | 22.3 | 1.67
5418 | 0 | 0 | 0 | 21.6 | 1.67
5419 | 0 | 0 | 0 | 22 | 3.33
5420 | 0 | 0 | 0 | 21.3 | 2.22
5421 | 0 | 0 | 0 | 21.7 | 4.44
5422 | 0 | 0 | 0 | 20.3 | 2.78
5423 | 0 | 0 | 0 | 19.8 | 2.78
5424 | 0 | 0 | 0 | 19.3 | 4.17
5425 | 0 | 0 | 0 | 19 | 1.67
5426 | 0 | 0 | 0 | 18.8 | 1.67
5427 | 0 | 0 | 0 | 18.9 | 2.22
5428 | 0 | 0 | 0 | 19.2 | 1.11
5429 | 0 | 2.8 | 0 | 19.2 | 2.78
5430 | 36.1 | 55.6 | 0 | 19.3 | 4.44
5431 | 91.7 | 111.1 | 0 | 19.8 | 2.78
5432 | 247.2 | 233.3 | 22.1 | 20.7 | 2.22
5433 | 469.4 | 325 | 179.6 | 22.7 | 3.33
5434 | 555.6 | 330.6 | 242.5 | 23.7 | 4.44
5435 | 627.8 | 402.8 | 226.9 | 25.6 | 7.22
5436 | 647.2 | 433.3 | 215.7 | 26.6 | 5.56
5437 | 658.3 | 416.7 | 260.5 | 27.1 | 4.44
5438 | 450 | 294.4 | 193.4 | 27.7 | 6.11
5439 | 350 | 219.4 | 207.4 | 27.8 | 5
5440 | 152.8 | 111.1 | 100.2 | 27.3 | 5
5441 | 100 | 22.2 | 395.9 | 26.6 | 5.56
5442 | 0 | 0 | 0 | 24.9 | 3.33
5443 | 0 | 0 | 0 | 22.5 | 2.78
5444 | 0 | 0 | 0 | 20.3 | 3.33
5445 | 0 | 0 | 0 | 20.3 | 2.78
5446 | 0 | 0 | 0 | 20.2 | 2.78
5447 | 0 | 0 | 0 | 20.1 | 2.22
5448 | 0 | 0 | 0 | 20.1 | 4.44
5449 | 0 | 0 | 0 | 20 | 2.22
5450 | 0 | 0 | 0 | 19.7 | 2.78
5451 | 0 | 0 | 0 | 19.6 | 2.22
5452 | 0 | 0 | 0 | 19.6 | 3.33
5453 | 0 | 11.1 | 0 | 19.2 | 2.22
5454 | 108.3 | 91.7 | 94.7 | 19.4 | 2.22
5455 | 247.2 | 197.2 | 120.5 | 19.9 | 2.78
5456 | 347.2 | 311.1 | 57.4 | 21.8 | 3.89
5457 | 422.2 | 425 | 0 | 22.9 | 4.44
5458 | 441.7 | 425 | 18 | 24 | 4.44
5459 | 466.7 | 497.2 | 0 | 24 | 3.33
5460 | 586.1 | 483.3 | 103.6 | 24.8 | 2.78
5461 | 708.3 | 480.6 | 245.5 | 26 | 3.33
5462 | 658.3 | 394.4 | 328.2 | 26.8 | 5
5463 | 450 | 258.3 | 304.6 | 26.6 | 2.78
5464 | 305.6 | 122.2 | 441.9 | 25.7 | 2.78
5465 | 100 | 36.1 | 363.2 | 25.2 | 3.33
5466 | 0 | 0 | 0 | 23.2 | 4.44
5467 | 0 | 0 | 0 | 22.5 | 1.67
5468 | 0 | 0 | 0 | 22 | 1.67
5469 | 0 | 0 | 0 | 22 | 1.67
5470 | 0 | 0 | 0 | 21.5 | 3.33
5471 | 0 | 0 | 0 | 21.3 | 2.22
5472 | 0 | 0 | 0 | 21.3 | 4.72
5473 | 0 | 0 | 0 | 20.9 | 4.44
5474 | 0 | 0 | 0 | 20.2 | 2.78
5475 | 0 | 0 | 0 | 20 | 3.33
5476 | 0 | 0 | 0 | 19.5 | 2.78
5477 | 2.8 | 0 | 0 | 19 | 2.78
5478 | 147.2 | 63.9 | 390.8 | 19.2 | 2.78
5479 | 319.4 | 233.3 | 207.9 | 20.5 | 2.22
5480 | 483.3 | 313.9 | 269.5 | 22.2 | 5
5481 | 594.4 | 380.6 | 266.1 | 23.1 | 5
5482 | 783.3 | 308.3 | 512 | 24 | 5
5483 | 836.1 | 313.9 | 526.5 | 25.8 | 4.44
5484 | 680.6 | 413.9 | 268.9 | 27 | 5.56
5485 | 761.1 | 344.4 | 449.1 | 27.3 | 6.11
5486 | 700 | 286.1 | 514.9 | 28.2 | 5.56
5487 | 544.4 | 213.9 | 525.8 | 28.9 | 4.44
5488 | 355.6 | 147.2 | 503.1 | 28.4 | 2.78
5489 | 127.8 | 69.4 | 333.7 | 28 | 3.89
5490 | 2.8 | 0 | 0 | 26.9 | 3.33
5491 | 0 | 0 | 0 | 26 | 2.22
5492 | 0 | 0 | 0 | 25 | 2.78
5493 | 0 | 0 | 0 | 24 | 3.33
5494 | 0 | 0 | 0 | 22.5 | 2.78
5495 | 0 | 0 | 0 | 22.6 | 3.89
5496 | 0 | 0 | 0 | 21.9 | 5
5497 | 0 | 0 | 0 | 20.9 | 2.22
5498 | 0 | 0 | 0 | 20.6 | 3.33
5499 | 0 | 0 | 0 | 20.2 | 2.22
5500 | 0 | 0 | 0 | 19.7 | 3.61
5501 | 0 | 0 | 0 | 19.4 | 3.33
5502 | 33.3 | 33.3 | 0 | 19.6 | 3.61
5503 | 119.4 | 116.7 | 6.7 | 20.2 | 3.33
5504 | 158.3 | 172.2 | 0 | 20.7 | 3.89
5505 | 247.2 | 283.3 | 0 | 21.5 | 4.44
5506 | 416.7 | 352.8 | 68.9 | 22.6 | 5
5507 | 797.2 | 541.7 | 257.7 | 24.9 | 5
5508 | 841.7 | 380.6 | 464.9 | 26.4 | 4.44
5509 | 686.1 | 391.7 | 317.4 | 26.8 | 3.33
5510 | 541.7 | 383.3 | 197 | 27.4 | 3.61
5511 | 450 | 300 | 238.8 | 27.7 | 3.33
5512 | 402.8 | 177.8 | 544.4 | 27.7 | 3.33
5513 | 138.9 | 97.2 | 239.9 | 27 | 4.17
5514 | 2.8 | 5.6 | 0 | 26.2 | 3.33
5515 | 0 | 0 | 0 | 25.2 | 3.33
5516 | 0 | 0 | 0 | 24.4 | 2.5
5517 | 0 | 0 | 0 | 23.5 | 2.22
5518 | 0 | 0 | 0 | 23.1 | 2.22
5519 | 0 | 0 | 0 | 21.8 | 2.78
5520 | 0 | 0 | 0 | 21 | 5.28
5521 | 0 | 0 | 0 | 20.5 | 3.65
5522 | 0 | 0 | 0 | 19.8 | 3.79
5523 | 0 | 0 | 0 | 19.7 | 3.44
5524 | 0 | 0 | 0 | 19.2 | 3.48
5525 | 0.5 | 2.8 | 0 | 18.9 | 3.57
5526 | 64.4 | 83.3 | 181.6 | 19.2 | 3.34
5527 | 194.2 | 188.9 | 188.7 | 19.8 | 3.5
5528 | 321.4 | 263.9 | 275.2 | 22.1 | 3.9
5529 | 666.7 | 383.3 | 352.7 | 23.5 | 4.33
5530 | 691.7 | 477.8 | 230.6 | 25.2 | 4.55
5531 | 897.2 | 547.2 | 352.9 | 25.2 | 4.5
5532 | 505.6 | 447.2 | 58.8 | 25.6 | 4.72
5533 | 541.7 | 472.2 | 74.9 | 25.8 | 4.44
5534 | 600 | 369.4 | 287 | 26.1 | 4.17
5535 | 302.8 | 263.9 | 62 | 26 | 3.89
5536 | 244.4 | 180.6 | 154.9 | 26 | 3.89
5537 | 72.2 | 41.7 | 177.1 | 25.6 | 3.33
5538 | 2.8 | 0 | 0 | 24.7 | 3.33
5539 | 0 | 0 | 0 | 24.2 | 1.94
5540 | 0 | 0 | 0 | 24.8 | 2.78
5541 | 0 | 0 | 0 | 23.2 | 2.78
5542 | 0 | 0 | 0 | 22.3 | 3.89
5543 | 0 | 0 | 0 | 21.2 | 4.44
5544 | 0 | 0 | 0 | 21 | 5.56
5545 | 0 | 0 | 0 | 20.3 | 3.33
5546 | 0 | 0 | 0 | 19.9 | 3.61
5547 | 0 | 0 | 0 | 19.6 | 2.78
5548 | 0 | 0 | 0 | 19.2 | 4.44
5549 | 2.8 | 0 | 0 | 18.6 | 3.89
5550 | 119.4 | 80.6 | 226.9 | 18.7 | 2.22
5551 | 341.7 | 188.9 | 371.1 | 19.9 | 3.33
5552 | 413.9 | 302.8 | 177.2 | 21.5 | 4.44
5553 | 661.1 | 341.7 | 397.8 | 22.9 | 4.44
5554 | 697.2 | 477.8 | 236.6 | 24.8 | 2.78
5555 | 680.6 | 494.4 | 187.7 | 25.9 | 5
5556 | 627.8 | 397.2 | 232.5 | 26.4 | 4.17
5557 | 538.9 | 300 | 257.6 | 25.9 | 4.44
5558 | 488.9 | 266.7 | 276.7 | 27.6 | 3.89
5559 | 258.3 | 208.3 | 79.7 | 26.3 | 3.33
5560 | 166.7 | 138.9 | 67.5 | 26.7 | 4.17
5561 | 50 | 52.8 | 0 | 25 | 3.61
5562 | 0 | 0 | 0 | 23.3 | 4.17
5563 | 0 | 0 | 0 | 22.9 | 4.17
5564 | 0 | 0 | 0 | 22.1 | 3.33
5565 | 0 | 0 | 0 | 21.7 | 1.94
5566 | 0 | 0 | 0 | 21.7 | 2.78
5567 | 0 | 0 | 0 | 21.4 | 3.33
5568 | 0 | 0 | 0 | 21 | 5.83
5569 | 0 | 0 | 0 | 20.7 | 2.78
5570 | 0 | 0 | 0 | 20 | 2.78
5571 | 0 | 0 | 0 | 19.5 | 2.22
5572 | 0 | 0 | 0 | 19.5 | 1.67
5573 | 0 | 0 | 0 | 18.8 | 1.67
5574 | 47.2 | 36.1 | 65.3 | 18.8 | 1.94
5575 | 158.3 | 152.8 | 13.5 | 20.1 | 1.67
5576 | 322.2 | 325 | 0 | 21.3 | 2.22
5577 | 305.6 | 319.4 | 0 | 22.7 | 5
5578 | 225 | 222.2 | 3 | 23.6 | 4.44
5579 | 236.1 | 269.4 | 0 | 24 | 4.17
5580 | 477.8 | 488.9 | 0 | 24.1 | 4.17
5581 | 625 | 538.9 | 92.9 | 25.1 | 4.17
5582 | 544.4 | 380.6 | 204.2 | 26.1 | 3.89
5583 | 358.3 | 213.9 | 230.6 | 26.2 | 5.56
5584 | 191.7 | 130.6 | 148.8 | 26.2 | 5.56
5585 | 100 | 36.1 | 375.3 | 25.6 | 4.44
5586 | 5.6 | 0 | 0 | 23.8 | 4.17
5587 | 0 | 0 | 0 | 22.6 | 2.78
5588 | 0 | 0 | 0 | 22.5 | 2.22
5589 | 0 | 0 | 0 | 21.9 | 2.22
5590 | 0 | 0 | 0 | 21.5 | 1.94
5591 | 0 | 0 | 0 | 21.1 | 2.78
5592 | 0 | 0 | 0 | 20.7 | 6.11
5593 | 0 | 0 | 0 | 20.3 | 4.17
5594 | 0 | 0 | 0 | 20 | 2.78
5595 | 0 | 0 | 0 | 19.9 | 2.22
5596 | 0 | 0 | 0 | 19.3 | 2.78
5597 | 0 | 0 | 0 | 19 | 2.78
5598 | 61.1 | 36.1 | 147.9 | 19.2 | 2.22
5599 | 163.9 | 161.1 | 6.8 | 20.6 | 3.89
5600 | 180.6 | 213.9 | 0 | 22 | 3.89
5601 | 258.3 | 261.1 | 0 | 22.5 | 3.89
5602 | 458.3 | 400 | 62.9 | 24.8 | 4.17
5603 | 655.6 | 511.1 | 145.7 | 25.5 | 4.44
5604 | 600 | 422.2 | 179.3 | 27 | 3.89
5605 | 558.3 | 344.4 | 230.8 | 27.3 | 2.78
5606 | 616.7 | 291.7 | 405.1 | 27.5 | 3.33
5607 | 525 | 230.6 | 470.4 | 28.2 | 3.33
5608 | 313.9 | 152.8 | 393 | 28 | 3.33
5609 | 116.7 | 86.1 | 180.8 | 27.2 | 3.61
5610 | 0 | 5.6 | 0 | 26.1 | 3.33
5611 | 0 | 0 | 0 | 24.8 | 2.78
5612 | 0 | 0 | 0 | 24.2 | 1.67
5613 | 0 | 0 | 0 | 23.8 | 1.67
5614 | 0 | 0 | 0 | 23 | 2.22
5615 | 0 | 0 | 0 | 22.2 | 2.78
5616 | 0 | 0 | 0 | 21.4 | 6.39
5617 | 0 | 0 | 0 | 20.6 | 3.33
5618 | 0 | 0 | 0 | 19.6 | 2.78
5619 | 0 | 0 | 0 | 19.3 | 1.67
5620 | 0 | 0 | 0 | 18.4 | 1.94
5621 | 0 | 0 | 0 | 18.2 | 1.67
5622 | 122.2 | 38.9 | 374.3 | 18.6 | 1.11
5623 | 336.1 | 116.7 | 536.5 | 21 | 1.67
5624 | 516.7 | 152.8 | 582 | 22.6 | 3.33
5625 | 719.4 | 161.1 | 696.4 | 24 | 3.33
5626 | 836.1 | 194.4 | 692.5 | 25.7 | 3.89
5627 | 725 | 352.8 | 375.5 | 26.4 | 3.33
5628 | 711.1 | 413.9 | 299.8 | 27.5 | 2.78
5629 | 608.3 | 347.2 | 281.8 | 27.6 | 2.78
5630 | 658.3 | 288.9 | 460.8 | 28.3 | 2.78
5631 | 438.9 | 213.9 | 359.9 | 28.8 | 2.78
5632 | 341.7 | 133.3 | 509.4 | 27.9 | 2.22
5633 | 127.8 | 41.7 | 374.3 | 28 | 2.22
5634 | 2.8 | 0 | 0 | 27 | 1.39
5635 | 0 | 0 | 0 | 26.7 | 0.83
5636 | 0 | 0 | 0 | 26.1 | 1.11
5637 | 0 | 0 | 0 | 25.5 | 1.39
5638 | 0 | 0 | 0 | 24.4 | 1.67
5639 | 0 | 0 | 0 | 24 | 1.67
5640 | 0 | 0 | 0 | 20.79 | 6.67
5641 | 0 | 0 | 0 | 20.45 | 1.11
5642 | 0 | 0 | 0 | 20.16 | 1.11
5643 | 0 | 0 | 0 | 19.98 | 1.67
5644 | 0 | 0 | 0 | 19.77 | 1.94
5645 | 2.8 | 0 | 0 | 19.56 | 1.67
5646 | 133.3 | 38.9 | 371.3 | 19.64 | 1.11
5647 | 291.7 | 169.4 | 299.5 | 20.34 | 0.83
5648 | 500 | 255.6 | 391.4 | 21.52 | 1.11
5649 | 444 | 317.8 | 294 | 22.75 | 1.39
5650 | 518 | 366.3 | 235.7 | 23.92 | 2.22
5651 | 638.9 | 402.8 | 238.3 | 24.86 | 1.94
5652 | 772.2 | 325 | 451.3 | 25.52 | 2.22
5653 | 744.4 | 280.6 | 500.8 | 25.8 | 2.22
5654 | 580.6 | 241.7 | 422.9 | 26.16 | 1.67
5655 | 558.3 | 147.2 | 658.2 | 25.85 | 2.22
5656 | 350 | 111.1 | 585.4 | 25.58 | 2.22
5657 | 88.9 | 36.1 | 316.8 | 24.94 | 1.94
5658 | 0 | 0 | 0 | 27.3 | 1.11
5659 | 0 | 0 | 0 | 26.2 | 0.83
5660 | 0 | 0 | 0 | 26.6 | 0
5661 | 0 | 0 | 0 | 25.4 | 0
5662 | 0 | 0 | 0 | 25.1 | 0
5663 | 0 | 0 | 0 | 23.5 | 1.39
5664 | 0 | 0 | 0 | 20.79 | 6.94
5665 | 0 | 0 | 0 | 20.45 | 2.78
5666 | 0 | 0 | 0 | 20.16 | 3.06
5667 | 0 | 0 | 0 | 19.98 | 0
5668 | 0 | 0 | 0 | 19.77 | 2.22
5669 | 0 | 0 | 0 | 19.56 | 2.5
5670 | 80.6 | 36.1 | 268.8 | 19.64 | 1.67
5671 | 111.1 | 111.1 | 0 | 20.34 | 1.67
5672 | 366.7 | 219.4 | 236 | 21.52 | 2.78
5673 | 555.6 | 400 | 194.2 | 22.75 | 1.67
5674 | 566.7 | 447.2 | 129 | 23.92 | 1.67
5675 | 672.2 | 472.2 | 201.9 | 24.86 | 1.67
5676 | 705.6 | 388.9 | 319.6 | 25.52 | 1.67
5677 | 863.9 | 286.1 | 624 | 25.8 | 1.67
5678 | 627.8 | 250 | 471.7 | 26.16 | 1.67
5679 | 483.3 | 283.3 | 320.6 | 25.85 | 2.22
5680 | 208.3 | 163.9 | 109.2 | 25.58 | 2.22
5681 | 125 | 83.3 | 252 | 24.94 | 1.39
5682 | 2.8 | 0 | 0 | 28.5 | 1.67
5683 | 0 | 0 | 0 | 26.2 | 1.67
5684 | 0 | 0 | 0 | 25 | 1.67
5685 | 0 | 0 | 0 | 24.2 | 2.78
5686 | 0 | 0 | 0 | 21.2 | 2.78
5687 | 0 | 0 | 0 | 21.4 | 1.39
5688 | 0 | 0 | 0 | 22.2 | 7.22
5689 | 0 | 0 | 0 | 20.7 | 2.78
5690 | 0 | 0 | 0 | 20.4 | 3.33
5691 | 0 | 0 | 0 | 20.2 | 4.44
5692 | 0 | 0 | 0 | 20.1 | 4.44
5693 | 2.8 | 2.8 | 0 | 19.8 | 4.17
5694 | 27.8 | 36.1 | 0 | 19.9 | 3.33
5695 | 119.4 | 169.4 | 0 | 20.8 | 3.89
5696 | 494.4 | 272.2 | 356.6 | 21.9 | 3.33
5697 | 608.3 | 363.9 | 305.4 | 23.5 | 3.33
5698 | 750 | 313.9 | 471.2 | 24.8 | 2.78
5699 | 713.9 | 527.8 | 187.9 | 25.8 | 2.78
5700 | 633.3 | 530.6 | 103.8 | 26.3 | 3.33
5701 | 683.3 | 377.8 | 330.1 | 27 | 2.78
5702 | 602.8 | 300 | 378.3 | 27.8 | 3.33
5703 | 441.7 | 211.1 | 370 | 27.8 | 2.78
5704 | 297.2 | 133.3 | 403.5 | 27.7 | 2.78
5705 | 111.1 | 52.8 | 355.5 | 27.7 | 2.78
5706 | 5.6 | 0 | 0 | 26.7 | 2.78
5707 | 0 | 0 | 0 | 25.8 | 1.11
5708 | 0 | 0 | 0 | 25.2 | 0.28
5709 | 0 | 0 | 0 | 24.6 | 0.56
5710 | 0 | 0 | 0 | 24 | 1.11
5711 | 0 | 0 | 0 | 23.3 | 1.39
5712 | 0 | 0 | 0 | 21.3 | 7.5
5713 | 0 | 0 | 0 | 20.5 | 0.83
5714 | 0 | 0 | 0 | 20.2 | 1.11
5715 | 0 | 0 | 0 | 20 | 1.94
5716 | 0 | 0 | 0 | 19.7 | 0.56
5717 | 2.8 | 0 | 0 | 19 | 1.11
5718 | 97.2 | 83.3 | 85.3 | 19.2 | 1.67
5719 | 325 | 136.1 | 466.3 | 20.2 | 1.67
5720 | 308.3 | 230.6 | 125 | 22 | 2.22
5721 | 627.8 | 311.1 | 396 | 22.7 | 2.78
5722 | 744.4 | 283.3 | 498.4 | 24.4 | 2.78
5723 | 872.2 | 261.1 | 617.3 | 25.7 | 2.78
5724 | 644.4 | 336.1 | 311.4 | 26.7 | 2.22
5725 | 716.7 | 336.1 | 411.4 | 27.4 | 2.22
5726 | 725 | 238.9 | 607.9 | 27.2 | 1.67
5727 | 575 | 197.2 | 607 | 27.9 | 1.67
5728 | 297.2 | 136.1 | 397.7 | 28 | 1.67
5729 | 77.8 | 50 | 170.6 | 27.2 | 2.22
5730 | 0 | 0 | 0 | 26.8 | 1.39
5731 | 0 | 0 | 0 | 25.7 | 1.11
5732 | 0 | 0 | 0 | 25.2 | 1.11
5733 | 0 | 0 | 0 | 24.9 | 1.39
5734 | 0 | 0 | 0 | 23.2 | 1.39
5735 | 0 | 0 | 0 | 22.6 | 1.94
5736 | 0 | 0 | 0 | 20.79 | 7.78
5737 | 0 | 0 | 0 | 20.45 | 2.78
5738 | 0 | 0 | 0 | 20.16 | 3.89
5739 | 0 | 0 | 0 | 19.98 | 3.89
5740 | 0 | 0 | 0 | 19.77 | 2.78
5741 | 0 | 0 | 0 | 19.56 | 2.78
5742 | 75 | 47.2 | 172 | 19.64 | 2.78
5743 | 247.2 | 183.3 | 158.1 | 20.34 | 2.78
5744 | 438.9 | 294.4 | 232.4 | 21.52 | 1.94
5745 | 569.4 | 361.1 | 260.7 | 22.75 | 2.22
5746 | 791.7 | 480.6 | 336.5 | 23.92 | 1.94
5747 | 841.7 | 444.4 | 401.4 | 24.86 | 1.94
5748 | 847.2 | 433.3 | 418.2 | 25.52 | 2.78
5749 | 750 | 363.9 | 417.6 | 25.8 | 2.22
5750 | 511.1 | 300 | 264.2 | 26.16 | 2.22
5751 | 333.3 | 211.1 | 196.6 | 25.85 | 1.94
5752 | 183.3 | 188.9 | 0 | 25.58 | 1.11
5753 | 66.7 | 63.9 | 17.2 | 24.94 | 0.83
5754 | 2.8 | 0 | 0 | 25.6 | 0
5755 | 0 | 0 | 0 | 24.8 | 1.11
5756 | 0 | 0 | 0 | 24.3 | 1.11
5757 | 0 | 0 | 0 | 23.6 | 0.56
5758 | 0 | 0 | 0 | 23.7 | 0.83
5759 | 0 | 0 | 0 | 23.2 | 1.39
5760 | 0 | 0 | 0 | 22.6 | 8.06
5761 | 0 | 0 | 0 | 21.9 | 2.22
5762 | 0 | 0 | 0 | 21.4 | 1.94
5763 | 0 | 0 | 0 | 20.9 | 1.67
5764 | 0 | 0 | 0 | 20.5 | 1.67
5765 | 0 | 0 | 0 | 20.3 | 1.94
5766 | 41.7 | 50 | 0 | 20.5 | 1.67
5767 | 188.9 | 166.7 | 55.1 | 21.1 | 1.67
5768 | 475 | 230.6 | 393.8 | 22.1 | 1.67
5769 | 711.1 | 200 | 640.1 | 23.6 | 1.94
5770 | 675 | 338.9 | 363.7 | 25.5 | 2.78
5771 | 650 | 458.3 | 193.8 | 26 | 2.78
5772 | 638.9 | 377.8 | 264 | 26.1 | 2.22
5773 | 800 | 369.4 | 465.9 | 27 | 1.67
5774 | 713.9 | 302.8 | 514.9 | 27.9 | 1.11
5775 | 525 | 236.1 | 465.4 | 28.5 | 1.67
5776 | 375 | 197.2 | 441.1 | 28.3 | 1.39
5777 | 125 | 69.4 | 346.7 | 27.9 | 1.67
5778 | 0 | 0 | 0 | 27 | 1.67
5779 | 0 | 0 | 0 | 26.3 | 1.67
5780 | 0 | 0 | 0 | 25.5 | 1.39
5781 | 0 | 0 | 0 | 24.7 | 0
5782 | 0 | 0 | 0 | 24.2 | 0
5783 | 0 | 0 | 0 | 23.3 | 2.22
5784 | 0 | 0 | 0 | 23.5 | 8.33
5785 | 0 | 0 | 0 | 23.2 | 0
5786 | 0 | 0 | 0 | 22.8 | 3.89
5787 | 0 | 0 | 0 | 22 | 2.78
5788 | 0 | 0 | 0 | 21.7 | 3.33
5789 | 0 | 0 | 0 | 21.5 | 2.22
5790 | 116.7 | 66.7 | 314.7 | 21.4 | 2.5
5791 | 333.3 | 105.6 | 566.7 | 22.2 | 2.78
5792 | 438.9 | 191.7 | 398.8 | 23.2 | 2.78
5793 | 719.4 | 155.6 | 706.8 | 25.2 | 2.78
5794 | 766.7 | 225 | 586.5 | 26.3 | 2.78
5795 | 838.9 | 316.7 | 528.2 | 26.6 | 2.78
5796 | 786.1 | 463.9 | 325.9 | 28 | 2.78
5797 | 597.2 | 347.2 | 270.7 | 28.6 | 3.33
5798 | 472.2 | 241.7 | 289 | 29 | 2.22
5799 | 355.6 | 172.2 | 295.8 | 29.1 | 2.78
5800 | 255.6 | 163.9 | 228.1 | 28.8 | 2.78
5801 | 80.6 | 80.6 | 0 | 28.8 | 1.11
5802 | 0 | 2.8 | 0 | 28.4 | 1.11
5803 | 0 | 0 | 0 | 24.4 | 0
5804 | 0 | 0 | 0 | 23.1 | 3.89
5805 | 0 | 0 | 0 | 23 | 3.89
5806 | 0 | 0 | 0 | 23.3 | 0
5807 | 0 | 0 | 0 | 23.4 | 0
5808 | 0 | 0 | 0 | 23.5 | 8.61
5809 | 0 | 0 | 0 | 23 | 1.67
5810 | 0 | 0 | 0 | 22.7 | 2.78
5811 | 0 | 0 | 0 | 22.2 | 2.22
5812 | 0 | 0 | 0 | 21.5 | 2.22
5813 | 0 | 2.8 | 0 | 21.2 | 2.22
5814 | 80.6 | 63.9 | 105.8 | 20.6 | 2.78
5815 | 347.2 | 122.2 | 561.3 | 21.1 | 2.78
5816 | 558.3 | 138.9 | 677.7 | 23.9 | 2.22
5817 | 702.8 | 230.6 | 592.5 | 25.1 | 2.5
5818 | 819.4 | 430.6 | 421.3 | 26.7 | 2.5
5819 | 738.9 | 472.2 | 269.9 | 26.7 | 1.11
5820 | 658.3 | 455.6 | 205.2 | 28.5 | 1.94
5821 | 547.2 | 463.9 | 90.3 | 28.1 | 1.39
5822 | 411.1 | 383.3 | 34.9 | 28.7 | 1.11
5823 | 236.1 | 261.1 | 0 | 29 | 1.67
5824 | 188.9 | 197.2 | 0 | 28.7 | 0.56
5825 | 47.2 | 61.1 | 0 | 28.6 | 0
5826 | 0 | 0 | 0 | 26.9 | 0
5827 | 0 | 0 | 0 | 26.2 | 0
5828 | 0 | 0 | 0 | 25.6 | 0
5829 | 0 | 0 | 0 | 25 | 1.67
5830 | 0 | 0 | 0 | 24.4 | 0
5831 | 0 | 0 | 0 | 23.7 | 2.22
5832 | 0 | 0 | 0 | 23 | 0.28
5833 | 0 | 0 | 0 | 22.4 | 3.33
5834 | 0 | 0 | 0 | 21.8 | 3.33
5835 | 0 | 0 | 0 | 21 | 2.78
5836 | 0 | 0 | 0 | 20.5 | 3.33
5837 | 2.8 | 0 | 0 | 20.4 | 3.33
5838 | 25 | 16.7 | 53.3 | 20.4 | 3.89
5839 | 150 | 117.3 | 205.1 | 20.6 | 3.33
5840 | 302.8 | 209.1 | 252 | 21.3 | 3.89
5841 | 427.8 | 300 | 160.5 | 23.3 | 3.89
5842 | 369.4 | 277.8 | 99.4 | 23.4 | 4.44
5843 | 511.1 | 369.4 | 143.5 | 24.5 | 3.89
5844 | 791.7 | 383.3 | 413.5 | 25.4 | 4.44
5845 | 791.7 | 330.6 | 500 | 27.1 | 5.56
5846 | 536.1 | 269.4 | 334.9 | 27.1 | 5
5847 | 338.9 | 183.3 | 251.7 | 26.5 | 3.89
5848 | 222.2 | 122.2 | 250.2 | 26.4 | 3.33
5849 | 55.6 | 47.2 | 53.3 | 21.5 | 4.44
5850 | 2.8 | 2.8 | 0 | 21.3 | 4.44
5851 | 0 | 0 | 0 | 21.3 | 2.78
5852 | 0 | 0 | 0 | 21.7 | 3.33
5853 | 0 | 0 | 0 | 21.6 | 3.89
5854 | 0 | 0 | 0 | 21.5 | 3.33
5855 | 0 | 0 | 0 | 21 | 3.33
5856 | 0 | 0 | 0 | 21 | 0.56
5857 | 0 | 0 | 0 | 21 | 3.33
5858 | 0 | 0 | 0 | 20.9 | 3.33
5859 | 0 | 0 | 0 | 20.9 | 3.89
5860 | 0 | 0 | 0 | 20.8 | 3.89
5861 | 0 | 0 | 0 | 20.2 | 3.33
5862 | 72.2 | 27.1 | 186.4 | 20.3 | 3.33
5863 | 202.8 | 117.3 | 205.1 | 20.8 | 3.33
5864 | 511.1 | 252.8 | 418.7 | 22.6 | 3.89
5865 | 519.4 | 336.1 | 230.5 | 24.1 | 3.89
5866 | 855.6 | 344.4 | 554.6 | 25.1 | 4.44
5867 | 700 | 413.9 | 289.9 | 25.8 | 5.56
5868 | 419.4 | 338.9 | 81.6 | 25.2 | 5.56
5869 | 511.1 | 397.2 | 123.6 | 25.8 | 4.44
5870 | 516.7 | 361.1 | 195.6 | 27.2 | 3.89
5871 | 413.9 | 283.3 | 211.6 | 26.7 | 3.89
5872 | 158.3 | 138.9 | 48.8 | 26.2 | 3.89
5873 | 58.3 | 55.6 | 17.9 | 25.2 | 3.33
5874 | 0 | 2.8 | 0 | 24 | 2.78
5875 | 0 | 0 | 0 | 23.8 | 3.33
5876 | 0 | 0 | 0 | 23.2 | 3.33
5877 | 0 | 0 | 0 | 22.6 | 5.56
5878 | 0 | 0 | 0 | 21.2 | 3.89
5879 | 0 | 0 | 0 | 21 | 2.78
5880 | 0 | 0 | 0 | 20.9 | 0.83
5881 | 0 | 0 | 0 | 20.7 | 3.33
5882 | 0 | 0 | 0 | 20.3 | 3.33
5883 | 0 | 0 | 0 | 20.3 | 3.33
5884 | 0 | 0 | 0 | 20.2 | 3.33
5885 | 0 | 0 | 0 | 20 | 3.33
5886 | 63.9 | 22.2 | 271.5 | 20.1 | 3.33
5887 | 294.4 | 116.7 | 447.4 | 21 | 3.89
5888 | 555.6 | 158.3 | 644.8 | 23.3 | 5.56
5889 | 719.4 | 250 | 590.8 | 24.8 | 5.56
5890 | 663.9 | 372.2 | 316.7 | 25.3 | 7.78
5891 | 741.7 | 427.8 | 318.3 | 24.7 | 6.11
5892 | 372.2 | 291.7 | 81.7 | 26.3 | 6.11
5893 | 613.9 | 444.4 | 184 | 26.8 | 6.67
5894 | 711.1 | 391.7 | 402 | 27.4 | 5
5895 | 377.8 | 297.2 | 130.8 | 25.4 | 5.56
5896 | 263.9 | 177.8 | 216.7 | 25.4 | 6.11
5897 | 66.7 | 36.1 | 199.1 | 24.8 | 5.56
5898 | 0 | 0 | 0 | 23.8 | 3.89
5899 | 0 | 0 | 0 | 23 | 3.89
5900 | 0 | 0 | 0 | 22.7 | 3.89
5901 | 0 | 0 | 0 | 22.7 | 3.89
5902 | 0 | 0 | 0 | 22.3 | 3.33
5903 | 0 | 0 | 0 | 21.9 | 3.33
5904 | 0 | 0 | 0 | 21.5 | 1.11
5905 | 0 | 0 | 0 | 21.2 | 3.33
5906 | 0 | 0 | 0 | 20.8 | 3.89
5907 | 0 | 0 | 0 | 20.7 | 3.33
5908 | 0 | 0 | 0 | 20.7 | 3.89
5909 | 2.8 | 0 | 0 | 20.6 | 3.33
5910 | 83.3 | 41.7 | 274.1 | 20.7 | 3.89
5911 | 250 | 158.3 | 231.4 | 21.6 | 3.33
5912 | 400 | 211.1 | 307.1 | 23.2 | 3.89
5913 | 494.4 | 269.4 | 283.5 | 24.7 | 5.56
5914 | 580.6 | 352.8 | 247.6 | 25.3 | 2.78
5915 | 527.8 | 341.7 | 188.9 | 25.7 | 2.78
5916 | 822.2 | 411.1 | 417.2 | 25.8 | 2.78
5917 | 563.9 | 425 | 151 | 26.1 | 2.22
5918 | 425 | 344.4 | 101.5 | 25.2 | 2.78
5919 | 394.4 | 219.4 | 284.5 | 25.8 | 2.78
5920 | 225 | 116.7 | 273.5 | 26.2 | 3.33
5921 | 69.4 | 44.4 | 164.4 | 23.7 | 5.56
5922 | 0 | 0 | 0 | 23.1 | 3.89
5923 | 0 | 0 | 0 | 22.3 | 2.78
5924 | 0 | 0 | 0 | 21.9 | 2.78
5925 | 0 | 0 | 0 | 21.9 | 3.06
5926 | 0 | 0 | 0 | 21.7 | 4.44
5927 | 0 | 0 | 0 | 21.2 | 3.89
5928 | 0 | 0 | 0 | 20.5 | 1.39
5929 | 0 | 0 | 0 | 20.3 | 3.33
5930 | 0 | 0 | 0 | 20 | 3.89
5931 | 0 | 0 | 0 | 20.1 | 3.33
5932 | 0 | 0 | 0 | 20.2 | 2.78
5933 | 0 | 0 | 0 | 20.2 | 3.33
5934 | 48.5 | 22.2 | 186.4 | 20.1 | 2.78
5935 | 188.2 | 122.2 | 205.1 | 21.3 | 3.33
5936 | 486.1 | 230.6 | 416.2 | 22.7 | 3.89
5937 | 569.6 | 275 | 363.6 | 24.1 | 4.44
5938 | 741.7 | 369.4 | 404.9 | 25.2 | 3.33
5939 | 655.6 | 397.2 | 262.3 | 26.5 | 5
5940 | 791.7 | 355.6 | 442.9 | 27.2 | 4.44
5941 | 863.9 | 302.8 | 610.4 | 27.6 | 5
5942 | 494.4 | 386.1 | 136.6 | 27.1 | 4.44
5943 | 397.2 | 300 | 158.4 | 26.7 | 5.56
5944 | 202.8 | 158.3 | 112.5 | 26.2 | 5.56
5945 | 36.1 | 30.6 | 36.9 | 24.8 | 3.89
5946 | 0 | 0 | 0 | 23.2 | 5.56
5947 | 0 | 0 | 0 | 22.9 | 3.89
5948 | 0 | 0 | 0 | 22.6 | 3.33
5949 | 0 | 0 | 0 | 22 | 3.33
5950 | 0 | 0 | 0 | 21.6 | 3.33
5951 | 0 | 0 | 0 | 21.4 | 3.33
5952 | 0 | 0 | 0 | 21.2 | 1.67
5953 | 0 | 0 | 0 | 21 | 3.33
5954 | 0 | 0 | 0 | 20.6 | 3.33
5955 | 0 | 0 | 0 | 20.4 | 3.33
5956 | 0 | 0 | 0 | 20.4 | 2.78
5957 | 0 | 0 | 0 | 20.5 | 2.78
5958 | 33.3 | 13.9 | 130.3 | 20.6 | 3.33
5959 | 72.2 | 41.7 | 77.6 | 20.6 | 3.33
5960 | 347.2 | 241.7 | 172.2 | 22 | 3.89
5961 | 586.1 | 336.1 | 315.7 | 24 | 3.33
5962 | 591.7 | 388.9 | 220.8 | 24.6 | 3.33
5963 | 641.7 | 458.3 | 186.3 | 25.5 | 3.33
5964 | 577.8 | 427.8 | 152.5 | 26 | 3.33
5965 | 352.8 | 275 | 84.7 | 25.4 | 3.89
5966 | 302.8 | 230.6 | 91.2 | 25 | 3.33
5967 | 233.3 | 191.7 | 68 | 25 | 3.33
5968 | 161.1 | 122.2 | 98.8 | 24.6 | 3.33
5969 | 55.6 | 47.2 | 55.9 | 24 | 3.33
5970 | 2.8 | 0 | 0 | 24.26 | 3.33
5971 | 0 | 0 | 0 | 23.76 | 3.89
5972 | 0 | 0 | 0 | 23.44 | 2.22
5973 | 0 | 0 | 0 | 22.91 | 3.33
5974 | 0 | 0 | 0 | 22.38 | 2.78
5975 | 0 | 0 | 0 | 21.96 | 2.78
5976 | 0 | 0 | 0 | 20 | 1.94
5977 | 0 | 0 | 0 | 20 | 2.78
5978 | 0 | 0 | 0 | 20 | 3.33
5979 | 0 | 0 | 0 | 20.1 | 2.78
5980 | 0 | 0 | 0 | 20.1 | 2.78
5981 | 0 | 0 | 0 | 20 | 2.78
5982 | 33.3 | 19.4 | 94 | 20.1 | 1.94
5983 | 155.6 | 108.3 | 120.3 | 20.8 | 2.78
5984 | 200 | 152.8 | 77.2 | 21.3 | 3.89
5985 | 427.8 | 316.7 | 140.5 | 22.5 | 3.33
5986 | 475 | 361.1 | 124.1 | 23.9 | 3.33
5987 | 536.1 | 413.9 | 124.3 | 25.1 | 4.44
5988 | 480.6 | 333.3 | 149.8 | 25.4 | 4.44
5989 | 380.6 | 313.9 | 72.7 | 24.9 | 3.33
5990 | 413.9 | 311.1 | 130 | 25.1 | 3.89
5991 | 433.3 | 275 | 258.8 | 22 | 3.33
5992 | 211.1 | 158.3 | 134.5 | 22.8 | 2.78
5993 | 72.2 | 52.8 | 131.6 | 21.7 | 2.78
5994 | 2.8 | 2.8 | 0 | 21.7 | 2.78
5995 | 0 | 0 | 0 | 21.4 | 2.78
5996 | 0 | 0 | 0 | 21.4 | 2.78
5997 | 0 | 0 | 0 | 21 | 2.78
5998 | 0 | 0 | 0 | 20.5 | 3.33
5999 | 0 | 0 | 0 | 20.1 | 2.78
6000 | 0 | 0 | 0 | 20.1 | 2.22
6001 | 0 | 0 | 0 | 20.1 | 3.33
6002 | 0 | 0 | 0 | 19.9 | 3.33
6003 | 0 | 0 | 0 | 19.9 | 3.33
6004 | 0 | 0 | 0 | 19.9 | 3.33
6005 | 0 | 0 | 0 | 19.7 | 3.33
6006 | 69.4 | 41.7 | 189.9 | 19.8 | 3.33
6007 | 183.3 | 141.7 | 106.5 | 20.4 | 3.33
6008 | 280.6 | 211.1 | 113.7 | 21.7 | 3.33
6009 | 397.2 | 300 | 123.1 | 22.9 | 3.33
6010 | 361.1 | 300 | 66.7 | 24.4 | 4.44
6011 | 347.2 | 275 | 73.5 | 24.9 | 5
6012 | 694.4 | 430.6 | 268.7 | 25.8 | 3.33
6013 | 522.2 | 302.8 | 239.4 | 24.9 | 4.44
6014 | 577.8 | 313.9 | 334.1 | 26.1 | 5.56
6015 | 488.9 | 227.8 | 427.7 | 26.3 | 4.44
6016 | 216.7 | 113.9 | 262.8 | 26.4 | 3.89
6017 | 72.2 | 36.1 | 246.8 | 23.4 | 3.89
6018 | 11.1 | 2.8 | 0 | 23 | 3.33
6019 | 0 | 0 | 0 | 22.3 | 2.22
6020 | 0 | 0 | 0 | 22 | 1.94
6021 | 0 | 0 | 0 | 21.9 | 3.33
6022 | 0 | 0 | 0 | 21.5 | 3.33
6023 | 0 | 0 | 0 | 20.8 | 3.89
6024 | 0 | 0 | 0 | 20 | 2.5
6025 | 0 | 0 | 0 | 19.6 | 3.33
6026 | 0 | 0 | 0 | 19.4 | 3.33
6027 | 0 | 0 | 0 | 19.4 | 2.22
6028 | 0 | 0 | 0 | 19.4 | 2.22
6029 | 2.8 | 0 | 0 | 19.3 | 2.22
6030 | 77.8 | 25 | 363.6 | 19.4 | 2.78
6031 | 263.9 | 141.7 | 313.6 | 20.7 | 2.22
6032 | 327.8 | 216.7 | 182.3 | 22.2 | 3.33
6033 | 663.9 | 258.3 | 514.2 | 23.5 | 3.89
6034 | 572.2 | 325 | 270.1 | 25.2 | 3.33
6035 | 558.3 | 305.6 | 257.7 | 24.7 | 3.89
6036 | 497.2 | 377.8 | 121.7 | 25.6 | 3.89
6037 | 455.6 | 280.6 | 191.2 | 26.2 | 3.33
6038 | 491.7 | 300 | 243 | 25.7 | 3.33
6039 | 538.9 | 191.7 | 569.8 | 25.3 | 3.89
6040 | 236.1 | 125 | 285.1 | 25.3 | 3.33
6041 | 25 | 16.7 | 57.5 | 24 | 3.33
6042 | 0 | 0 | 0 | 22.5 | 2.22
6043 | 0 | 0 | 0 | 22.2 | 1.11
6044 | 0 | 0 | 0 | 21.6 | 4.44
6045 | 0 | 0 | 0 | 21.3 | 1.67
6046 | 0 | 0 | 0 | 20.8 | 2.78
6047 | 0 | 0 | 0 | 20.3 | 2.22
6048 | 0 | 0 | 0 | 20.2 | 2.78
6049 | 0 | 0 | 0 | 19.7 | 2.78
6050 | 0 | 0 | 0 | 19.2 | 2.78
6051 | 0 | 0 | 0 | 18.7 | 2.22
6052 | 0 | 0 | 0 | 18.7 | 1.94
6053 | 2.8 | 0 | 0 | 18.7 | 2.22
6054 | 105.6 | 30.6 | 359.3 | 18.8 | 1.94
6055 | 327.8 | 108.3 | 565 | 19.7 | 2.22
6056 | 352.8 | 252.8 | 164.4 | 21.5 | 2.78
6057 | 494.4 | 305.6 | 239.9 | 22 | 3.33
6058 | 463.9 | 369.4 | 103.3 | 22.9 | 2.22
6059 | 727.8 | 361.1 | 374.1 | 24.2 | 2.78
6060 | 858.3 | 430.6 | 436.5 | 24.9 | 2.78
6061 | 705.6 | 319.4 | 422.3 | 26.7 | 2.78
6062 | 400 | 311.1 | 112.9 | 26.2 | 3.33
6063 | 488.9 | 297.2 | 315.2 | 26.2 | 2.78
6064 | 183.3 | 166.7 | 42.9 | 25.9 | 2.78
6065 | 75 | 52.8 | 155 | 25.2 | 2.78
6066 | 2.8 | 2.8 | 0 | 24.6 | 1.11
6067 | 0 | 0 | 0 | 23.7 | 0
6068 | 0 | 0 | 0 | 23.2 | 0
6069 | 0 | 0 | 0 | 22.7 | 0
6070 | 0 | 0 | 0 | 22.2 | 0
6071 | 0 | 0 | 0 | 22 | 0
6072 | 0 | 0 | 0 | 21.2 | 3.06
6073 | 0 | 0 | 0 | 20.3 | 3.33
6074 | 0 | 0 | 0 | 19.7 | 1.39
6075 | 0 | 0 | 0 | 19.3 | 1.39
6076 | 0 | 0 | 0 | 19 | 1.39
6077 | 2.8 | 0 | 0 | 19 | 1.39
6078 | 72.2 | 52.8 | 137.1 | 19.2 | 1.67
6079 | 169.4 | 150 | 50.2 | 20.1 | 3.33
6080 | 355.6 | 263.9 | 151 | 22.1 | 2.78
6081 | 688.9 | 352.8 | 427.4 | 23.3 | 2.78
6082 | 897.2 | 261.1 | 696.5 | 24.8 | 1.67
6083 | 888.9 | 363.9 | 536.3 | 25.7 | 2.78
6084 | 800 | 341.7 | 468.2 | 26.9 | 2.78
6085 | 619.4 | 325 | 322.4 | 27.3 | 1.67
6086 | 616.7 | 258.3 | 455.7 | 27.6 | 3.33
6087 | 513.9 | 186.1 | 540.1 | 27.7 | 3.33
6088 | 355.6 | 100 | 660.3 | 27.8 | 2.22
6089 | 122.2 | 41.7 | 355 | 27.3 | 1.67
6090 | 2.8 | 0 | 0 | 24.8 | 0.56
6091 | 0 | 0 | 0 | 24.8 | 0.56
6092 | 0 | 0 | 0 | 24.2 | 0
6093 | 0 | 0 | 0 | 23.3 | 0
6094 | 0 | 0 | 0 | 23 | 0
6095 | 0 | 0 | 0 | 22.3 | 2.22
6096 | 0 | 0 | 0 | 21.8 | 3.33
6097 | 0 | 0 | 0 | 21.6 | 3.33
6098 | 0 | 0 | 0 | 21.3 | 2.78
6099 | 0 | 0 | 0 | 20.4 | 1.67
6100 | 0 | 0 | 0 | 20.1 | 1.67
6101 | 0 | 0 | 0 | 19.9 | 1.39
6102 | 47.2 | 22.2 | 178.1 | 20.1 | 0.83
6103 | 186.1 | 130.6 | 144.1 | 20.6 | 0.83
6104 | 386.1 | 275 | 183.5 | 21.2 | 2.22
6105 | 383.3 | 291.7 | 116.8 | 22.5 | 2.78
6106 | 469.4 | 383.3 | 94.4 | 23.9 | 2.22
6107 | 586.1 | 425 | 164.8 | 25.1 | 2.78
6108 | 669.4 | 447.2 | 227.3 | 26.1 | 2.78
6109 | 500 | 408.3 | 100.5 | 26.6 | 2.78
6110 | 1219.4 | 338.9 | 920.7 | 26.8 | 2.78
6111 | 1008.3 | 241.7 | 865.1 | 27.3 | 2.78
6112 | 413.9 | 158.3 | 662.7 | 26.8 | 2.78
6113 | 713.9 | 58.3 | 350.6 | 26.1 | 2.78
6114 | 163.9 | 2.8 | 0 | 24.5 | 1.67
6115 | 0 | 0 | 0 | 24.2 | 2.22
6116 | 0 | 0 | 0 | 23.5 | 2.22
6117 | 0 | 0 | 0 | 23 | 1.67
6118 | 0 | 0 | 0 | 22.9 | 1.67
6119 | 0 | 0 | 0 | 22.7 | 1.67
6120 | 0 | 0 | 0 | 22.5 | 3.61
6121 | 0 | 0 | 0 | 21.9 | 0.56
6122 | 0 | 0 | 0 | 21 | 2.78
6123 | 0 | 0 | 0 | 20.6 | 2.78
6124 | 0 | 0 | 0 | 20.4 | 1.94
6125 | 0 | 0 | 0 | 20 | 1.94
6126 | 63.9 | 41.7 | 160.1 | 20 | 1.67
6127 | 247.2 | 138.9 | 282 | 21 | 1.94
6128 | 538.9 | 202.8 | 556.3 | 22.7 | 3.33
6129 | 641.7 | 336.1 | 389.8 | 23.9 | 2.78
6130 | 722.2 | 463.9 | 283.6 | 25.1 | 2.22
6131 | 725 | 416.7 | 315.7 | 25.6 | 2.78
6132 | 661.1 | 444.4 | 221.8 | 26.4 | 2.78
6133 | 547.2 | 366.7 | 198.2 | 26.7 | 2.5
6134 | 472.2 | 341.7 | 166.6 | 26.9 | 2.78
6135 | 388.9 | 272.2 | 193.1 | 27.1 | 2.22
6136 | 241.7 | 186.1 | 144.6 | 27.5 | 1.67
6137 | 44.4 | 75 | 0 | 26.4 | 2.78
6138 | 0 | 2.8 | 0 | 25 | 1.67
6139 | 0 | 0 | 0 | 24.6 | 1.39
6140 | 0 | 0 | 0 | 24.5 | 1.39
6141 | 0 | 0 | 0 | 22.9 | 0
6142 | 0 | 0 | 0 | 22.6 | 0
6143 | 0 | 0 | 0 | 22.1 | 0
6144 | 0 | 0 | 0 | 21.4 | 3.89
6145 | 0 | 0 | 0 | 21.3 | 0.83
6146 | 0 | 0 | 0 | 20.4 | 0
6147 | 0 | 0 | 0 | 19.9 | 0
6148 | 0 | 0 | 0 | 19.6 | 0
6149 | 0 | 0 | 0 | 19.2 | 1.11
6150 | 94.4 | 38.9 | 341.6 | 19.2 | 1.11
6151 | 325 | 105.6 | 573.3 | 21 | 1.67
6152 | 580.6 | 166.7 | 686.5 | 23.2 | 1.67
6153 | 769.4 | 172.2 | 763.2 | 24.6 | 1.67
6154 | 686.1 | 288.9 | 436.7 | 26.5 | 0
6155 | 830.6 | 311.1 | 532.5 | 27.1 | 0
6156 | 669.4 | 327.8 | 350.3 | 27.1 | 0.83
6157 | 838.9 | 352.8 | 534.4 | 28.6 | 1.11
6158 | 711.1 | 258.3 | 578.6 | 29.1 | 1.67
6159 | 586.1 | 227.8 | 594.4 | 29.2 | 2.22
6160 | 263.9 | 138.9 | 326.6 | 28.5 | 2.78
6161 | 58.3 | 50 | 60.7 | 27.7 | 2.78
6162 | 0 | 2.8 | 0 | 26.7 | 0
6163 | 0 | 0 | 0 | 26.2 | 0
6164 | 0 | 0 | 0 | 26.2 | 0
6165 | 0 | 0 | 0 | 24.4 | 0
6166 | 0 | 0 | 0 | 23.2 | 0
6167 | 0 | 0 | 0 | 22.9 | 0.83
6168 | 0 | 0 | 0 | 22.4 | 4.17
6169 | 0 | 0 | 0 | 22.1 | 1.67
6170 | 0 | 0 | 0 | 22.1 | 1.67
6171 | 0 | 0 | 0 | 21.1 | 1.67
6172 | 0 | 0 | 0 | 21.1 | 1.67
6173 | 0 | 0 | 0 | 20.4 | 1.67
6174 | 48.5 | 41.7 | 186.4 | 20.5 | 1.67
6175 | 188.2 | 155.6 | 205.1 | 22.2 | 0.56
6176 | 362.9 | 208.3 | 252 | 23.7 | 1.67
6177 | 758.3 | 244.4 | 657.8 | 25.2 | 2.22
6178 | 500 | 302.8 | 217.1 | 26.1 | 2.78
6179 | 583.3 | 338.9 | 250.9 | 26.5 | 1.94
6180 | 827.8 | 341.7 | 499 | 27.1 | 2.5
6181 | 825 | 241.7 | 642.2 | 28.1 | 2.78
6182 | 769.4 | 175 | 760.9 | 28 | 2.78
6183 | 602.8 | 161.1 | 734.3 | 28.7 | 1.67
6184 | 313.9 | 133.3 | 473.5 | 28.7 | 2.5
6185 | 80.6 | 55.6 | 184.1 | 28.2 | 1.67
6186 | 0 | 2.8 | 0 | 26.2 | 1.67
6187 | 0 | 0 | 0 | 25.7 | 1.39
6188 | 0 | 0 | 0 | 24.7 | 0
6189 | 0 | 0 | 0 | 24.3 | 0
6190 | 0 | 0 | 0 | 24 | 0
6191 | 0 | 0 | 0 | 23.7 | 2.22
6192 | 0 | 0 | 0 | 22.9 | 4.44
6193 | 0 | 0 | 0 | 22.2 | 2.22
6194 | 0 | 0 | 0 | 21.7 | 1.67
6195 | 0 | 0 | 0 | 21.4 | 1.94
6196 | 0 | 0 | 0 | 21.4 | 1.67
6197 | 0 | 0 | 0 | 21.4 | 1.94
6198 | 27.8 | 38.9 | 0 | 21.6 | 1.67
6199 | 213.9 | 177.8 | 95.1 | 22.2 | 1.94
6200 | 200 | 200 | 0 | 22.7 | 2.22
6201 | 369.4 | 347.2 | 28.5 | 24.2 | 2.22
6202 | 680.6 | 441.7 | 263.4 | 25.5 | 2.78
6203 | 827.8 | 427.8 | 411.2 | 26 | 2.78
6204 | 694.4 | 419.4 | 282.7 | 27.5 | 2.78
6205 | 411.1 | 302.8 | 119.4 | 26.7 | 2.78
6206 | 222.2 | 175 | 60.6 | 26.9 | 2.78
6207 | 141.7 | 147.2 | 0 | 27.5 | 4.44
6208 | 188.9 | 166.7 | 58.5 | 26.5 | 2.22
6209 | 2.8 | 33.3 | 0 | 26.4 | 2.22
6210 | 0 | 2.8 | 0 | 24.26 | 2.78
6211 | 0 | 0 | 0 | 23.76 | 2.22
6212 | 0 | 0 | 0 | 23.44 | 0
6213 | 0 | 0 | 0 | 22.91 | 3.33
6214 | 0 | 0 | 0 | 22.38 | 0
6215 | 0 | 0 | 0 | 21.96 | 1.67
6216 | 0 | 0 | 0 | 20.5 | 4.72
6217 | 0 | 0 | 0 | 20.4 | 2.78
6218 | 0 | 0 | 0 | 20.3 | 2.22
6219 | 0 | 0 | 0 | 20.3 | 2.22
6220 | 0 | 0 | 0 | 20.2 | 2.22
6221 | 0 | 0 | 0 | 20 | 2.22
6222 | 22.2 | 25 | 0 | 20.1 | 1.94
6223 | 166.7 | 138.9 | 73.4 | 20.5 | 2.22
6224 | 344.4 | 277.8 | 111.4 | 22.6 | 1.67
6225 | 700 | 286.1 | 531.7 | 23.7 | 2.22
6226 | 794.4 | 305.6 | 539.9 | 25.2 | 3.33
6227 | 711.1 | 386.1 | 334.6 | 25.7 | 2.78
6228 | 755.6 | 477.8 | 286 | 26.6 | 2.78
6229 | 702.8 | 372.2 | 365 | 26.5 | 2.22
6230 | 600 | 294.4 | 392.5 | 25.6 | 2.22
6231 | 286.1 | 183.3 | 171.7 | 24.7 | 3.33
6232 | 33.3 | 58.3 | 0 | 23.3 | 2.22
6233 | 2.8 | 25 | 0 | 21.8 | 2.22
6234 | 0 | 2.8 | 0 | 24.26 | 2.22
6235 | 0 | 0 | 0 | 23.76 | 1.39
6236 | 0 | 0 | 0 | 23.44 | 0
6237 | 0 | 0 | 0 | 22.91 | 0
6238 | 0 | 0 | 0 | 22.38 | 3.33
6239 | 0 | 0 | 0 | 21.96 | 1.67
6240 | 0 | 0 | 0 | 19.9 | 5
6241 | 0 | 0 | 0 | 19.9 | 0
6242 | 0 | 0 | 0 | 19.9 | 0
6243 | 0 | 0 | 0 | 19.9 | 0
6244 | 0 | 0 | 0 | 19.9 | 1.11
6245 | 0 | 0 | 0 | 19.8 | 1.11
6246 | 22.2 | 25 | 0 | 19.9 | 1.67
6247 | 83.3 | 80.6 | 7.4 | 20.3 | 0
6248 | 213.9 | 186.1 | 46.5 | 21.5 | 0
6249 | 380.6 | 308.3 | 93 | 23.7 | 1.67
6250 | 691.7 | 405.6 | 316.4 | 24.9 | 2.78
6251 | 761.1 | 372.2 | 400.9 | 26.1 | 1.11
6252 | 727.8 | 338.9 | 400.9 | 26.9 | 1.94
6253 | 88.9 | 94.4 | 0 | 25.9 | 1.67
6254 | 133.3 | 125 | 10.7 | 22.4 | 0
6255 | 444.4 | 316.7 | 214 | 24.4 | 2.78
6256 | 258.3 | 180.6 | 206.4 | 24.5 | 1.39
6257 | 11.1 | 33.3 | 0 | 24.3 | 1.67
6258 | 0 | 2.8 | 0 | 24.2 | 0
6259 | 0 | 0 | 0 | 23.7 | 0
6260 | 0 | 0 | 0 | 23.5 | 0
6261 | 0 | 0 | 0 | 23.4 | 0
6262 | 0 | 0 | 0 | 21 | 1.67
6263 | 0 | 0 | 0 | 20.6 | 3.33
6264 | 0 | 0 | 0 | 20.6 | 5.28
6265 | 0 | 0 | 0 | 20.1 | 3.89
6266 | 0 | 0 | 0 | 20 | 2.78
6267 | 0 | 0 | 0 | 20 | 2.78
6268 | 0 | 0 | 0 | 20 | 2.78
6269 | 0 | 0 | 0 | 19.8 | 1.39
6270 | 11.1 | 16.7 | 0 | 19.9 | 0
6271 | 77.8 | 69.4 | 22.2 | 20.1 | 1.11
6272 | 222.2 | 197.2 | 42 | 20.6 | 1.11
6273 | 694.4 | 372.2 | 415.5 | 23.3 | 1.11
6274 | 936.1 | 213.9 | 800.1 | 24.8 | 2.22
6275 | 561.1 | 291.7 | 278.2 | 25.7 | 1.67
6276 | 675 | 297.2 | 390.1 | 26.7 | 1.11
6277 | 588.9 | 269.4 | 353.9 | 27.5 | 1.94
6278 | 775 | 291.7 | 623.3 | 27.7 | 1.67
6279 | 158.3 | 136.1 | 37.3 | 27.3 | 1.67
6280 | 27.8 | 25 | 7.4 | 25.2 | 0
6281 | 16.7 | 11.1 | 42.9 | 24.6 | 2.78
6282 | 0 | 0 | 0 | 23.2 | 1.67
6283 | 0 | 0 | 0 | 22.9 | 0
6284 | 0 | 0 | 0 | 22.9 | 1.11
6285 | 0 | 0 | 0 | 22.9 | 0
6286 | 0 | 0 | 0 | 23 | 0
6287 | 0 | 0 | 0 | 22.7 | 0
6288 | 0 | 0 | 0 | 22.6 | 5.56
6289 | 0 | 0 | 0 | 22.6 | 1.39
6290 | 0 | 0 | 0 | 22.3 | 1.11
6291 | 0 | 0 | 0 | 21.8 | 0.83
6292 | 0 | 0 | 0 | 21.4 | 1.94
6293 | 0 | 0 | 0 | 20.8 | 1.39
6294 | 5.6 | 27.1 | 186.4 | 20.8 | 1.11
6295 | 72.2 | 117.3 | 205.1 | 20.3 | 2.22
6296 | 344.4 | 209.1 | 252 | 21.8 | 1.67
6297 | 391.7 | 287.6 | 363.6 | 21.8 | 1.11
6298 | 419.4 | 331.5 | 353.3 | 23.9 | 1.39
6299 | 688.9 | 356.9 | 318.1 | 25.7 | 0
6300 | 858.3 | 355.2 | 311.8 | 26.9 | 1.94
6301 | 611.1 | 311.3 | 301.6 | 27.4 | 1.94
6302 | 655.6 | 274.1 | 335.1 | 28.1 | 1.94
6303 | 111.1 | 213.9 | 340.2 | 28.4 | 2.22
6304 | 50 | 125.8 | 246.7 | 25.9 | 0
6305 | 8.3 | 41 | 146.7 | 25.4 | 2.5
6306 | 0 | 1.3 | 0 | 24.8 | 2.22
6307 | 0 | 0 | 0 | 24.4 | 1.11
6308 | 0 | 0 | 0 | 24.3 | 0
6309 | 0 | 0 | 0 | 24 | 0
6310 | 0 | 0 | 0 | 23.5 | 0
6311 | 0 | 0 | 0 | 23 | 0
6312 | 0 | 0 | 0 | 23.1 | 5.83
6313 | 0 | 0 | 0 | 23.1 | 0
6314 | 0 | 0 | 0 | 22.9 | 0
6315 | 0 | 0 | 0 | 22.4 | 1.67
6316 | 0 | 0 | 0 | 21 | 2.78
6317 | 0 | 0 | 0 | 20.7 | 1.67
6318 | 33.3 | 27.1 | 186.4 | 20.7 | 1.67
6319 | 205.6 | 117.3 | 205.1 | 22.4 | 1.39
6320 | 505.6 | 209.1 | 252 | 24.8 | 1.39
6321 | 716.7 | 287.6 | 363.6 | 26.2 | 1.67
6322 | 850 | 331.5 | 353.3 | 26.8 | 2.78
6323 | 791.7 | 356.9 | 318.1 | 25.7 | 2.78
6324 | 894.4 | 355.2 | 311.8 | 28.2 | 2.22
6325 | 788.9 | 311.3 | 301.6 | 28.2 | 2.78
6326 | 697.2 | 274.1 | 335.1 | 28.3 | 3.33
6327 | 541.7 | 213.9 | 340.2 | 28.2 | 2.78
6328 | 255.6 | 125.8 | 246.7 | 27.9 | 2.78
6329 | 69.4 | 41 | 146.7 | 27 | 2.22
6330 | 0 | 1.3 | 0 | 26.1 | 2.22
6331 | 0 | 0 | 0 | 25.4 | 1.39
6332 | 0 | 0 | 0 | 25.2 | 0
6333 | 0 | 0 | 0 | 24.7 | 0
6334 | 0 | 0 | 0 | 23.7 | 0
6335 | 0 | 0 | 0 | 23.3 | 0
6336 | 0 | 0 | 0 | 22.3 | 6.11
6337 | 0 | 0 | 0 | 22.1 | 0
6338 | 0 | 0 | 0 | 21.8 | 0
6339 | 0 | 0 | 0 | 21.3 | 0
6340 | 0 | 0 | 0 | 21.4 | 0
6341 | 0 | 0 | 0 | 21.6 | 0
6342 | 22.2 | 16.7 | 44.5 | 21.6 | 0
6343 | 66.7 | 55.6 | 30 | 21.8 | 0
6344 | 213.9 | 158.3 | 94 | 24 | 0.56
6345 | 491.7 | 352.8 | 180.2 | 25.5 | 0
6346 | 600 | 391.7 | 232 | 26.6 | 1.11
6347 | 513.9 | 377.8 | 141.2 | 27.1 | 0
6348 | 333.3 | 258.3 | 77.8 | 27 | 1.39
6349 | 530.6 | 397.2 | 148.5 | 28 | 1.11
6350 | 636.1 | 277.8 | 464.9 | 27 | 0
6351 | 325 | 208.3 | 197.5 | 27.1 | 1.67
6352 | 225 | 122.2 | 277.4 | 25.9 | 1.39
6353 | 27.8 | 30.6 | 0 | 25.6 | 1.39
6354 | 0 | 0 | 0 | 25 | 0.83
6355 | 0 | 0 | 0 | 22.5 | 0.56
6356 | 0 | 0 | 0 | 22.5 | 2.78
6357 | 0 | 0 | 0 | 22.5 | 1.67
6358 | 0 | 0 | 0 | 22.5 | 0
6359 | 0 | 0 | 0 | 22.5 | 0
6360 | 0 | 0 | 0 | 22.1 | 6.39
6361 | 0 | 0 | 0 | 22 | 0.83
6362 | 0 | 0 | 0 | 21.7 | 0.83
6363 | 0 | 0 | 0 | 21.5 | 0.83
6364 | 0 | 0 | 0 | 21.5 | 1.39
6365 | 0 | 0 | 0 | 21.5 | 1.11
6366 | 33.3 | 30.6 | 22.5 | 21.5 | 1.67
6367 | 172.2 | 150 | 60.2 | 21.9 | 2.22
6368 | 269.4 | 244.4 | 42.4 | 23.2 | 1.67
6369 | 602.8 | 327.8 | 357.6 | 25 | 1.67
6370 | 719.4 | 327.8 | 437 | 26.9 | 1.67
6371 | 816.7 | 361.1 | 473.5 | 28.3 | 1.94
6372 | 800 | 350 | 467.7 | 27.9 | 2.22
6373 | 858.3 | 302.8 | 619.9 | 27.9 | 2.22
6374 | 730.6 | 247.2 | 628.5 | 28.9 | 2.22
6375 | 469.4 | 241.7 | 386.6 | 29 | 2.78
6376 | 188.9 | 155.6 | 90.4 | 28.7 | 2.78
6377 | 52.8 | 61.1 | 0 | 27.9 | 2.22
6378 | 0 | 2.8 | 0 | 26.9 | 2.22
6379 | 0 | 0 | 0 | 26.1 | 0
6380 | 0 | 0 | 0 | 25.9 | 0
6381 | 0 | 0 | 0 | 25.5 | 0
6382 | 0 | 0 | 0 | 24.5 | 0
6383 | 0 | 0 | 0 | 24 | 0
6384 | 0 | 0 | 0 | 23.2 | 6.67
6385 | 0 | 0 | 0 | 22.8 | 0
6386 | 0 | 0 | 0 | 22.4 | 1.67
6387 | 0 | 0 | 0 | 22.2 | 1.11
6388 | 0 | 0 | 0 | 22.1 | 0
6389 | 0 | 0 | 0 | 22.2 | 0
6390 | 22.2 | 11.1 | 91.4 | 22.2 | 1.11
6391 | 147.2 | 105.6 | 113.4 | 22.4 | 0.56
6392 | 394.4 | 236.1 | 269.5 | 23.9 | 1.11
6393 | 641.7 | 227.8 | 539.4 | 25.4 | 2.22
6394 | 700 | 272.2 | 478.2 | 26.2 | 2.78
6395 | 805.6 | 230.6 | 598.7 | 27.6 | 1.67
6396 | 858.3 | 252.8 | 630.6 | 28 | 0
6397 | 819.4 | 227.8 | 661.4 | 29.2 | 0
6398 | 755.6 | 166.7 | 767.4 | 29 | 2.22
6399 | 502.8 | 130.6 | 633.5 | 28.7 | 2.22
6400 | 236.1 | 94.4 | 385.7 | 28.8 | 1.67
6401 | 61.1 | 38.9 | 182.7 | 27.7 | 2.78
6402 | 0 | 0 | 0 | 26.5 | 1.11
6403 | 0 | 0 | 0 | 25.9 | 0.83
6404 | 0 | 0 | 0 | 25.4 | 0
6405 | 0 | 0 | 0 | 24.6 | 0.83
6406 | 0 | 0 | 0 | 23.6 | 0
6407 | 0 | 0 | 0 | 22.7 | 0
6408 | 0 | 0 | 0 | 22.2 | 6.94
6409 | 0 | 0 | 0 | 21.8 | 0
6410 | 0 | 0 | 0 | 21.2 | 0
6411 | 0 | 0 | 0 | 21.2 | 0
6412 | 0 | 0 | 0 | 21 | 0
6413 | 0 | 0 | 0 | 20.2 | 0
6414 | 47.2 | 22.2 | 208.3 | 20.7 | 0
6415 | 252.8 | 105.6 | 402.6 | 23.2 | 0
6416 | 558.3 | 138.9 | 716 | 25.2 | 0
6417 | 705.6 | 161.1 | 711.1 | 26.4 | 0
6418 | 891.7 | 194.4 | 781 | 26.6 | 0
6419 | 752.8 | 255.6 | 518.7 | 28.1 | 1.11
6420 | 713.9 | 269.4 | 463.7 | 28.6 | 1.11
6421 | 500 | 280.6 | 245.8 | 29 | 0
6422 | 186.1 | 136.1 | 65.3 | 28.5 | 1.67
6423 | 261.1 | 197.2 | 109.1 | 28.1 | 2.5
6424 | 155.6 | 113.9 | 114 | 27.8 | 2.78
6425 | 50 | 44.4 | 46.3 | 27.4 | 0
6426 | 0 | 0 | 0 | 27 | 0
6427 | 0 | 0 | 0 | 26.6 | 0
6428 | 0 | 0 | 0 | 26.1 | 0
6429 | 0 | 0 | 0 | 25.3 | 0
6430 | 0 | 0 | 0 | 24 | 0
6431 | 0 | 0 | 0 | 22.8 | 0
6432 | 0 | 0 | 0 | 22.7 | 7.22
6433 | 0 | 0 | 0 | 22.4 | 0
6434 | 0 | 0 | 0 | 21.6 | 0
6435 | 0 | 0 | 0 | 21 | 0
6436 | 0 | 0 | 0 | 21 | 0
6437 | 0 | 0 | 0 | 20.8 | 0
6438 | 55.6 | 36.1 | 164.2 | 21.1 | 0
6439 | 283.3 | 127.8 | 427.4 | 22.4 | 0
6440 | 530.6 | 188.9 | 584.9 | 25.2 | 0
6441 | 702.8 | 180.6 | 683.7 | 27.2 | 1.39
6442 | 833.3 | 197.2 | 714 | 27.6 | 0.56
6443 | 888.9 | 266.7 | 650.3 | 28.7 | 0.28
6444 | 836.1 | 275 | 586.5 | 29.7 | 0
6445 | 813.9 | 280.6 | 598.6 | 30.2 | 2.78
6446 | 666.7 | 263.9 | 527.3 | 29.7 | 0
6447 | 538.9 | 202.8 | 575.4 | 29.7 | 2.78
6448 | 369.4 | 166.7 | 557.1 | 29.1 | 2.78
6449 | 86.1 | 66.7 | 164.2 | 28.4 | 0
6450 | 0 | 0 | 0 | 25.9 | 2.22
6451 | 0 | 0 | 0 | 25.7 | 2.5
6452 | 0 | 0 | 0 | 25.4 | 2.22
6453 | 0 | 0 | 0 | 22.9 | 2.22
6454 | 0 | 0 | 0 | 22.9 | 2.22
6455 | 0 | 0 | 0 | 22.1 | 0.83
6456 | 0 | 0 | 0 | 22.1 | 7.5
6457 | 0 | 0 | 0 | 22.1 | 1.67
6458 | 0 | 0 | 0 | 22.1 | 1.67
6459 | 0 | 0 | 0 | 21.2 | 1.67
6460 | 0 | 0 | 0 | 20.7 | 2.22
6461 | 0 | 0 | 0 | 20.7 | 1.67
6462 | 33.3 | 11.1 | 190.2 | 20.7 | 1.67
6463 | 127.8 | 75 | 145.7 | 22 | 1.67
6464 | 372.2 | 250 | 209.9 | 23.2 | 1.67
6465 | 700 | 294.4 | 532.2 | 25 | 2.22
6466 | 825 | 294.4 | 596.7 | 26.4 | 2.22
6467 | 852.8 | 386.1 | 488.7 | 27.3 | 2.78
6468 | 538.9 | 416.7 | 128 | 27.6 | 2.22
6469 | 272.2 | 244.4 | 31.2 | 25.7 | 2.22
6470 | 313.9 | 288.9 | 32.8 | 25.3 | 2.22
6471 | 52.8 | 58.3 | 0 | 21.2 | 2.78
6472 | 25 | 13.9 | 30.7 | 20.7 | 2.78
6473 | 13.9 | 22.2 | 0 | 20.7 | 2.22
6474 | 0 | 0 | 0 | 20.6 | 1.67
6475 | 0 | 0 | 0 | 20.6 | 0
6476 | 0 | 0 | 0 | 20.6 | 0
6477 | 0 | 0 | 0 | 20.6 | 0
6478 | 0 | 0 | 0 | 21 | 0
6479 | 0 | 0 | 0 | 21.2 | 0
6480 | 0 | 0 | 0 | 21.2 | 7.78
6481 | 0 | 0 | 0 | 21.2 | 0
6482 | 0 | 0 | 0 | 21.2 | 0
6483 | 0 | 0 | 0 | 21.1 | 0
6484 | 0 | 0 | 0 | 21 | 0
6485 | 2.8 | 0 | 0 | 20.9 | 0
6486 | 105.6 | 33.3 | 271.2 | 21 | 0
6487 | 263.9 | 130.6 | 369.8 | 21.7 | 0
6488 | 144.4 | 111.1 | 57.4 | 22.5 | 0
6489 | 352.8 | 275 | 102.3 | 23.3 | 0
6490 | 466.7 | 400 | 75.1 | 23.9 | 2.22
6491 | 313.9 | 300 | 14.6 | 24.9 | 2.22
6492 | 372.2 | 330.6 | 43.7 | 25.5 | 1.94
6493 | 258.3 | 213.9 | 50.1 | 26.5 | 2.78
6494 | 477.8 | 330.6 | 193.7 | 22.8 | 3.33
6495 | 525 | 280.6 | 421 | 22.9 | 0
6496 | 116.7 | 100 | 46.2 | 23.5 | 2.22
6497 | 38.9 | 11.1 | 241.1 | 23.4 | 2.22
6498 | 0 | 0 | 0 | 23.4 | 2.78
6499 | 0 | 0 | 0 | 23.3 | 2.22
6500 | 0 | 0 | 0 | 22.3 | 1.94
6501 | 0 | 0 | 0 | 21.9 | 2.22
6502 | 0 | 0 | 0 | 21.5 | 1.94
6503 | 0 | 0 | 0 | 21.3 | 1.94
6504 | 0 | 0 | 0 | 21.3 | 8.06
6505 | 0 | 0 | 0 | 20.7 | 1.39
6506 | 0 | 0 | 0 | 20.6 | 1.39
6507 | 0 | 0 | 0 | 20.4 | 1.39
6508 | 0 | 0 | 0 | 20.3 | 1.39
6509 | 0 | 0 | 0 | 20 | 1.39
6510 | 47.2 | 25 | 195.6 | 20.1 | 0.83
6511 | 175 | 113.9 | 170.3 | 20.7 | 2.5
6512 | 350 | 227.8 | 211.2 | 22.6 | 1.67
6513 | 605.6 | 300 | 402.9 | 23.4 | 2.78
6514 | 583.3 | 327.8 | 288.7 | 24.2 | 2.78
6515 | 711.1 | 361.1 | 368 | 25.3 | 2.78
6516 | 711.1 | 350 | 379.7 | 24.9 | 2.78
6517 | 597.2 | 413.9 | 207.1 | 25.5 | 3.33
6518 | 513.9 | 266.7 | 326 | 25.4 | 2.78
6519 | 463.9 | 230.6 | 403.1 | 25.7 | 3.33
6520 | 219.4 | 119.4 | 278.6 | 24.8 | 3.33
6521 | 38.9 | 30.6 | 73.4 | 23.7 | 3.33
6522 | 0 | 0 | 0 | 22.8 | 3.33
6523 | 0 | 0 | 0 | 22.3 | 2.78
6524 | 0 | 0 | 0 | 21.9 | 2.5
6525 | 0 | 0 | 0 | 21.8 | 2.78
6526 | 0 | 0 | 0 | 21.7 | 2.22
6527 | 0 | 0 | 0 | 21.3 | 2.22
6528 | 0 | 0 | 0 | 20.8 | 8.33
6529 | 0 | 0 | 0 | 20.6 | 1.39
6530 | 0 | 0 | 0 | 20.5 | 1.39
6531 | 0 | 0 | 0 | 20.5 | 1.39
6532 | 0 | 0 | 0 | 20.5 | 1.39
6533 | 0 | 0 | 0 | 20.4 | 1.39
6534 | 27.8 | 8.3 | 173.6 | 20.6 | 1.39
6535 | 133.3 | 100 | 93.3 | 20.8 | 1.39
6536 | 236.1 | 183.3 | 91.5 | 22.71 | 0.56
6537 | 491.7 | 275 | 286.4 | 24.12 | 2.78
6538 | 555.6 | 350 | 232.7 | 25.21 | 2.78
6539 | 555.6 | 358.3 | 207.8 | 25.99 | 3.33
6540 | 472.2 | 225 | 260.5 | 26.66 | 3.33
6541 | 552.8 | 230.6 | 364.8 | 27 | 2.78
6542 | 466.7 | 219.4 | 326.8 | 26.76 | 2.22
6543 | 152.8 | 100 | 91.5 | 26.51 | 2.5
6544 | 308.3 | 88.9 | 614.4 | 26.11 | 2.22
6545 | 111.1 | 38.9 | 260.3 | 25.11 | 3.33
6546 | 0 | 0 | 0 | 24.26 | 3.33
6547 | 0 | 0 | 0 | 23.76 | 3.61
6548 | 0 | 0 | 0 | 23.44 | 3.33
6549 | 0 | 0 | 0 | 22.91 | 2.22
6550 | 0 | 0 | 0 | 22.38 | 1.67
6551 | 0 | 0 | 0 | 21.96 | 1.67
6552 | 0 | 0 | 0 | 20.4 | 0.28
6553 | 0 | 0 | 0 | 20.5 | 0
6554 | 0 | 0 | 0 | 20.5 | 1.67
6555 | 0 | 0 | 0 | 20.5 | 1.67
6556 | 0 | 0 | 0 | 20.6 | 1.67
6557 | 0 | 0 | 0 | 20.5 | 0
6558 | 61.1 | 30.6 | 276.9 | 20.6 | 2.22
6559 | 183.3 | 141.7 | 117.2 | 21.2 | 2.78
6560 | 583.3 | 252.8 | 574.7 | 22.7 | 2.78
6561 | 600 | 319.4 | 371.8 | 24 | 2.78
6562 | 719.4 | 297.2 | 479 | 25.7 | 3.89
6563 | 800 | 397.2 | 425.3 | 25.9 | 2.78
6564 | 713.9 | 419.4 | 310.9 | 25.9 | 2.78
6565 | 852.8 | 402.8 | 510.6 | 26.9 | 2.78
6566 | 391.7 | 236.1 | 206.2 | 23.9 | 3.33
6567 | 91.7 | 69.4 | 38.6 | 24.4 | 4.44
6568 | 105.6 | 80.6 | 70.3 | 23.7 | 5
6569 | 61.1 | 44.4 | 151 | 23.5 | 3.89
6570 | 0 | 0 | 0 | 23 | 2.78
6571 | 0 | 0 | 0 | 22.7 | 3.33
6572 | 0 | 0 | 0 | 22.2 | 2.78
6573 | 0 | 0 | 0 | 21.9 | 3.33
6574 | 0 | 0 | 0 | 21.7 | 2.78
6575 | 0 | 0 | 0 | 21.4 | 2.78
6576 | 0 | 0 | 0 | 21.4 | 0.56
6577 | 0 | 0 | 0 | 21.3 | 2.78
6578 | 0 | 0 | 0 | 21.2 | 0
6579 | 0 | 0 | 0 | 21.3 | 0
6580 | 0 | 0 | 0 | 21.4 | 2.78
6581 | 0 | 0 | 0 | 21.4 | 0
6582 | 19.4 | 2.8 | 153.3 | 21.5 | 2.22
6583 | 80.6 | 63.9 | 47.1 | 21.9 | 2.78
6584 | 275 | 238.9 | 63 | 22.6 | 2.22
6585 | 488.9 | 391.7 | 129.2 | 23.3 | 2.78
6586 | 488.9 | 394.4 | 107.4 | 24.3 | 2.78
6587 | 838.9 | 294.4 | 576.1 | 25.8 | 2.22
6588 | 944.4 | 383.3 | 593.8 | 25.9 | 2.22
6589 | 825 | 341.7 | 549.6 | 26.8 | 3.33
6590 | 866.7 | 236.1 | 837.9 | 27.3 | 2.78
6591 | 555.6 | 247.2 | 537.8 | 27 | 2.22
6592 | 102.8 | 77.8 | 70.7 | 24.6 | 2.78
6593 | 36.1 | 16.7 | 178.8 | 24.1 | 2.78
6594 | 0 | 0 | 0 | 23.6 | 2.78
6595 | 0 | 0 | 0 | 22.3 | 2.78
6596 | 0 | 0 | 0 | 22.4 | 2.22
6597 | 0 | 0 | 0 | 22 | 2.78
6598 | 0 | 0 | 0 | 22 | 2.22
6599 | 0 | 0 | 0 | 21.9 | 0
6600 | 0 | 0 | 0 | 22 | 0.83
6601 | 0 | 0 | 0 | 21.8 | 2.78
6602 | 0 | 0 | 0 | 21.8 | 1.67
6603 | 0 | 0 | 0 | 21.7 | 2.78
6604 | 0 | 0 | 0 | 21.7 | 2.22
6605 | 0 | 0 | 0 | 21.3 | 1.67
6606 | 47.2 | 25 | 207.4 | 21.3 | 2.22
6607 | 216.7 | 136.1 | 228.9 | 21.8 | 2.22
6608 | 425 | 258.3 | 291.7 | 24 | 2.22
6609 | 650 | 305.6 | 458.9 | 25.1 | 2.22
6610 | 586.1 | 316.7 | 307.1 | 26.2 | 3.33
6611 | 719.4 | 297.2 | 447.8 | 27.2 | 2.78
6612 | 788.9 | 344.4 | 471.4 | 27.6 | 2.22
6613 | 666.7 | 236.1 | 490.8 | 28.4 | 2.78
6614 | 838.9 | 216.7 | 829 | 29.2 | 2.78
6615 | 502.8 | 177.8 | 568.8 | 28.3 | 3.89
6616 | 133.3 | 111.1 | 63.1 | 25.5 | 3.33
6617 | 33.3 | 16.7 | 155.6 | 24.8 | 2.78
6618 | 0 | 0 | 0 | 23.6 | 2.78
6619 | 0 | 0 | 0 | 23.3 | 2.78
6620 | 0 | 0 | 0 | 21.6 | 2.78
6621 | 0 | 0 | 0 | 21.4 | 5.56
6622 | 0 | 0 | 0 | 21.4 | 3.33
6623 | 0 | 0 | 0 | 21.4 | 2.22
6624 | 0 | 0 | 0 | 21.4 | 1.11
6625 | 0 | 0 | 0 | 21.4 | 2.22
6626 | 0 | 0 | 0 | 21.4 | 2.22
6627 | 0 | 0 | 0 | 21.4 | 2.78
6628 | 0 | 0 | 0 | 21.2 | 2.78
6629 | 0 | 0 | 0 | 21.1 | 2.22
6630 | 52.8 | 8.3 | 275.6 | 21.1 | 1.67
6631 | 300 | 94.4 | 587 | 22.1 | 2.22
6632 | 488.9 | 186.1 | 531.7 | 23.9 | 2.78
6633 | 452.8 | 305.6 | 196.7 | 25.4 | 2.78
6634 | 630.6 | 355.6 | 314.2 | 26.2 | 2.78
6635 | 669.4 | 308.3 | 383.9 | 27.3 | 3.89
6636 | 900 | 236.1 | 705.7 | 27.9 | 4.44
6637 | 944.4 | 222.2 | 825.2 | 28.4 | 3.89
6638 | 808.3 | 213.9 | 794.1 | 28.4 | 4.44
6639 | 419.4 | 283.3 | 239 | 27.9 | 4.44
6640 | 177.8 | 155.6 | 63.5 | 26.6 | 3.33
6641 | 58.3 | 41.7 | 158 | 25.4 | 3.89
6642 | 0 | 0 | 0 | 24.7 | 2.78
6643 | 0 | 0 | 0 | 24.4 | 3.89
6644 | 0 | 0 | 0 | 23.1 | 4.44
6645 | 0 | 0 | 0 | 23.1 | 2.78
6646 | 0 | 0 | 0 | 22.9 | 3.89
6647 | 0 | 0 | 0 | 22.2 | 2.78
6648 | 0 | 0 | 0 | 21.4 | 1.39
6649 | 0 | 0 | 0 | 21 | 2.78
6650 | 0 | 0 | 0 | 20.6 | 1.67
6651 | 0 | 0 | 0 | 20.7 | 2.22
6652 | 0 | 0 | 0 | 20.9 | 1.67
6653 | 0 | 0 | 0 | 20.9 | 1.67
6654 | 80.6 | 44.4 | 269.5 | 21.2 | 1.67
6655 | 302.8 | 147.2 | 446.5 | 21.7 | 2.22
6656 | 469.4 | 280.6 | 332.8 | 23.5 | 1.67
6657 | 361.1 | 280.6 | 107.9 | 25 | 1.67
6658 | 716.7 | 372.2 | 394.5 | 26 | 2.78
6659 | 358.3 | 305.6 | 56.2 | 26.5 | 2.78
6660 | 613.9 | 402.8 | 224.9 | 26.2 | 2.78
6661 | 230.6 | 155.6 | 85.9 | 27.5 | 1.67
6662 | 119.4 | 122.2 | 0 | 25.9 | 2.78
6663 | 388.9 | 302.8 | 151.7 | 26.3 | 2.22
6664 | 241.7 | 138.9 | 295 | 24.1 | 3.33
6665 | 19.4 | 25 | 0 | 22.7 | 3.89
6666 | 0 | 0 | 0 | 22.3 | 2.22
6667 | 0 | 0 | 0 | 22.3 | 0
6668 | 0 | 0 | 0 | 22 | 2.22
6669 | 0 | 0 | 0 | 22.2 | 1.67
6670 | 0 | 0 | 0 | 21.8 | 2.78
6671 | 0 | 0 | 0 | 21.3 | 2.78
6672 | 0 | 0 | 0 | 21.3 | 1.67
6673 | 0 | 0 | 0 | 21.3 | 0
6674 | 0 | 0 | 0 | 20.9 | 2.22
6675 | 0 | 0 | 0 | 20.6 | 2.22
6676 | 0 | 0 | 0 | 20.6 | 1.67
6677 | 0 | 0 | 0 | 20.4 | 1.67
6678 | 13.9 | 19.4 | 0 | 20.5 | 0
6679 | 161.1 | 144.4 | 48.1 | 21.3 | 0
6680 | 177.8 | 186.1 | 0 | 22.9 | 1.67
6681 | 313.9 | 305.6 | 11.2 | 23.7 | 0
6682 | 500 | 408.3 | 105.3 | 23.8 | 2.22
6683 | 369.4 | 319.4 | 53.4 | 25 | 1.67
6684 | 747.2 | 477.8 | 287.8 | 26.9 | 2.22
6685 | 169.4 | 169.4 | 0 | 25.6 | 1.67
6686 | 536.1 | 333.3 | 272.4 | 26.3 | 3.33
6687 | 575 | 155.6 | 741.6 | 26.6 | 3.33
6688 | 377.8 | 97.2 | 750.7 | 26.3 | 3.33
6689 | 116.7 | 38.9 | 263.4 | 25.8 | 2.78
6690 | 0 | 0 | 0 | 25 | 2.22
6691 | 0 | 0 | 0 | 24.5 | 2.22
6692 | 0 | 0 | 0 | 23.9 | 2.22
6693 | 0 | 0 | 0 | 23.2 | 2.22
6694 | 0 | 0 | 0 | 23.1 | 1.67
6695 | 0 | 0 | 0 | 22 | 1.11
6696 | 0 | 0 | 0 | 21.7 | 1.94
6697 | 0 | 0 | 0 | 21.6 | 1.67
6698 | 0 | 0 | 0 | 21.3 | 2.22
6699 | 0 | 0 | 0 | 21.3 | 0
6700 | 0 | 0 | 0 | 21.3 | 1.67
6701 | 0 | 0 | 0 | 21 | 0
6702 | 41.7 | 36.1 | 55.2 | 21.4 | 2.22
6703 | 113.9 | 108.3 | 16.1 | 21.6 | 2.22
6704 | 275 | 258.3 | 29.6 | 21.5 | 2.22
6705 | 344.4 | 300 | 59.9 | 21.6 | 0
6706 | 369.4 | 302.8 | 76.7 | 22.8 | 1.67
6707 | 530.6 | 283.3 | 264.7 | 23.5 | 1.67
6708 | 863.9 | 300 | 603.6 | 25.1 | 1.11
6709 | 519.4 | 269.4 | 287.8 | 23.2 | 3.33
6710 | 294.4 | 250 | 59.9 | 22.7 | 1.67
6711 | 50 | 52.8 | 0 | 22.7 | 2.78
6712 | 69.4 | 69.4 | 0 | 22.6 | 2.22
6713 | 16.7 | 11.1 | 55.2 | 22.4 | 1.67
6714 | 0 | 0 | 0 | 22.2 | 1.11
6715 | 0 | 0 | 0 | 22.1 | 1.11
6716 | 0 | 0 | 0 | 22.1 | 0
6717 | 0 | 0 | 0 | 21.9 | 0
6718 | 0 | 0 | 0 | 21.9 | 0
6719 | 0 | 0 | 0 | 21.4 | 0
6720 | 0 | 0 | 0 | 21.3 | 2.22
6721 | 0 | 0 | 0 | 20.8 | 0
6722 | 0 | 0 | 0 | 20.6 | 0
6723 | 0 | 0 | 0 | 20.6 | 0
6724 | 0 | 0 | 0 | 20.7 | 1.67
6725 | 0 | 0 | 0 | 20.5 | 1.67
6726 | 25 | 25 | 0 | 20.6 | 0
6727 | 250 | 125 | 364.4 | 21.4 | 1.67
6728 | 433.3 | 258.3 | 311.6 | 24.4 | 1.67
6729 | 738.9 | 280.6 | 619.2 | 23.8 | 3.33
6730 | 905.6 | 277.8 | 724.5 | 25.7 | 2.22
6731 | 833.3 | 355.6 | 512.7 | 27 | 2.22
6732 | 902.8 | 322.2 | 623 | 27.7 | 1.67
6733 | 941.7 | 208.3 | 846.3 | 27.6 | 2.78
6734 | 838.9 | 183.3 | 885.6 | 28.3 | 1.67
6735 | 530.6 | 219.4 | 553.9 | 28.6 | 2.22
6736 | 261.1 | 169.4 | 267.3 | 27.8 | 2.78
6737 | 36.1 | 30.6 | 56.1 | 25.5 | 2.78
6738 | 0 | 0 | 0 | 23.8 | 2.78
6739 | 0 | 0 | 0 | 21.7 | 2.78
6740 | 0 | 0 | 0 | 21.2 | 2.78
6741 | 0 | 0 | 0 | 20.6 | 3.89
6742 | 0 | 0 | 0 | 20.5 | 2.22
6743 | 0 | 0 | 0 | 20 | 3.33
6744 | 0 | 0 | 0 | 20 | 2.5
6745 | 0 | 0 | 0 | 20.3 | 1.67
6746 | 0 | 0 | 0 | 20 | 1.67
6747 | 0 | 0 | 0 | 20 | 2.22
6748 | 0 | 0 | 0 | 20 | 1.67
6749 | 0 | 0 | 0 | 20.1 | 0
6750 | 25 | 16.7 | 85.5 | 20.2 | 0
6751 | 197.2 | 177.8 | 57 | 20.5 | 2.78
6752 | 222.2 | 211.1 | 19.9 | 21.4 | 2.22
6753 | 280.6 | 272.2 | 11.3 | 22.4 | 2.22
6754 | 397.2 | 375 | 25.7 | 23.4 | 2.78
6755 | 297.2 | 283.3 | 14.9 | 24.2 | 2.78
6756 | 100 | 102.8 | 0 | 24.4 | 3.33
6757 | 394.4 | 327.8 | 77.1 | 24.6 | 2.78
6758 | 294.4 | 291.7 | 3.8 | 25.6 | 2.22
6759 | 205.6 | 197.2 | 14.9 | 25.2 | 3.33
6760 | 88.9 | 97.2 | 0 | 23 | 6.11
6761 | 30.6 | 33.3 | 0 | 21.7 | 3.33
6762 | 0 | 0 | 0 | 21.7 | 2.78
6763 | 0 | 0 | 0 | 21.7 | 2.78
6764 | 0 | 0 | 0 | 21.8 | 2.22
6765 | 0 | 0 | 0 | 21.8 | 2.22
6766 | 0 | 0 | 0 | 21.7 | 2.78
6767 | 0 | 0 | 0 | 21.4 | 2.22
6768 | 0 | 0 | 0 | 21.2 | 2.78
6769 | 0 | 0 | 0 | 21 | 0
6770 | 0 | 0 | 0 | 20.7 | 0
6771 | 0 | 0 | 0 | 20.1 | 0
6772 | 0 | 0 | 0 | 20.2 | 0
6773 | 0 | 0 | 0 | 20.2 | 0
6774 | 61.1 | 47.2 | 144.8 | 20.2 | 0
6775 | 222.2 | 180.6 | 122.8 | 20.7 | 2.22
6776 | 294.4 | 225 | 124.5 | 22.1 | 0
6777 | 544.4 | 361.1 | 249.1 | 23.6 | 0
6778 | 630.6 | 413.9 | 251.4 | 24.6 | 1.67
6779 | 941.7 | 263.9 | 731 | 26.3 | 0
6780 | 816.7 | 361.1 | 491.3 | 26.8 | 2.78
6781 | 852.8 | 397.2 | 528.5 | 27.8 | 3.33
6782 | 550 | 366.7 | 249.1 | 27.9 | 2.78
6783 | 583.3 | 330.6 | 453.3 | 28.3 | 2.22
6784 | 358.3 | 216.7 | 417.4 | 27.9 | 2.78
6785 | 83.3 | 83.3 | 0 | 26.8 | 3.33
6786 | 0 | 0 | 0 | 25.5 | 2.78
6787 | 0 | 0 | 0 | 23.5 | 2.78
6788 | 0 | 0 | 0 | 22.2 | 2.78
6789 | 0 | 0 | 0 | 22 | 1.11
6790 | 0 | 0 | 0 | 21.8 | 0
6791 | 0 | 0 | 0 | 21.5 | 1.67
6792 | 0 | 0 | 0 | 21.5 | 3.06
6793 | 0 | 0 | 0 | 21.5 | 1.67
6794 | 0 | 0 | 0 | 21.6 | 1.67
6795 | 0 | 0 | 0 | 21.5 | 1.67
6796 | 0 | 0 | 0 | 21.5 | 2.22
6797 | 0 | 0 | 0 | 21.3 | 2.22
6798 | 30.6 | 33.3 | 0 | 21.3 | 1.67
6799 | 152.8 | 130.6 | 65.8 | 22 | 2.22
6800 | 386.1 | 300 | 155 | 23.6 | 2.78
6801 | 611.1 | 333.3 | 378.6 | 24.8 | 2.22
6802 | 619.4 | 319.4 | 349 | 25.8 | 1.11
6803 | 797.2 | 302.8 | 534.6 | 26.7 | 2.22
6804 | 422.2 | 275 | 159.2 | 25.6 | 2.22
6805 | 338.9 | 230.6 | 126 | 26.6 | 2.22
6806 | 83.3 | 75 | 11.4 | 25.7 | 1.67
6807 | 100 | 97.2 | 5 | 22 | 2.78
6808 | 30.6 | 30.6 | 0 | 21.6 | 2.78
6809 | 8.3 | 2.8 | 58.9 | 21.4 | 2.78
6810 | 0 | 0 | 0 | 21.4 | 2.22
6811 | 0 | 0 | 0 | 21.4 | 2.22
6812 | 0 | 0 | 0 | 21.6 | 1.67
6813 | 0 | 0 | 0 | 21.6 | 1.67
6814 | 0 | 0 | 0 | 21.4 | 2.78
6815 | 0 | 0 | 0 | 21 | 2.22
6816 | 0 | 0 | 0 | 21.12 | 3.33
6817 | 0 | 0 | 0 | 20.99 | 3.33
6818 | 0 | 0 | 0 | 20.82 | 3.33
6819 | 0 | 0 | 0 | 20.73 | 2.78
6820 | 0 | 0 | 0 | 20.65 | 1.67
6821 | 0 | 0 | 0 | 20.43 | 2.78
6822 | 22.2 | 16.7 | 59.9 | 20.52 | 0
6823 | 144.4 | 130.6 | 41.4 | 21.41 | 2.78
6824 | 413.9 | 241.7 | 311.1 | 23.09 | 2.78
6825 | 750 | 336.1 | 565.8 | 24.28 | 1.67
6826 | 511.1 | 383.3 | 149 | 25.49 | 2.22
6827 | 480.6 | 402.8 | 84.3 | 26.4 | 1.67
6828 | 777.8 | 508.3 | 292.1 | 26.82 | 1.67
6829 | 625 | 430.6 | 226.8 | 27.16 | 2.22
6830 | 538.9 | 338.9 | 273.4 | 26.99 | 2.78
6831 | 269.4 | 244.4 | 45.2 | 26.52 | 3.33
6832 | 211 | 25 | 275.5 | 25.46 | 5.56
6833 | 46.3 | 0 | 118.8 | 24.44 | 1.11
6834 | 0 | 0 | 0 | 21.3 | 1.67
6835 | 0 | 0 | 0 | 21.2 | 2.22
6836 | 0 | 0 | 0 | 21.2 | 0
6837 | 0 | 0 | 0 | 21.2 | 0
6838 | 0 | 0 | 0 | 21.3 | 0
6839 | 0 | 0 | 0 | 21.7 | 1.67
6840 | 0 | 0 | 0 | 21.7 | 3.61
6841 | 0 | 0 | 0 | 21.7 | 1.67
6842 | 0 | 0 | 0 | 21.7 | 1.67
6843 | 0 | 0 | 0 | 21.3 | 2.22
6844 | 0 | 0 | 0 | 21.3 | 2.22
6845 | 0 | 0 | 0 | 21 | 2.22
6846 | 19.4 | 16.7 | 30.5 | 20.9 | 2.22
6847 | 102.8 | 102.8 | 0 | 21.4 | 1.67
6848 | 288.9 | 252.8 | 65.5 | 23.1 | 2.22
6849 | 502.8 | 355.6 | 201.9 | 24.2 | 2.78
6850 | 763.9 | 413.9 | 409.3 | 25.7 | 2.22
6851 | 741.7 | 397.2 | 374.4 | 27.4 | 2.22
6852 | 819.4 | 441.7 | 410.6 | 27.4 | 2.22
6853 | 813.9 | 422.2 | 458.1 | 27.9 | 2.22
6854 | 716.7 | 369.4 | 476.1 | 26.8 | 2.22
6855 | 491.7 | 297.2 | 352.5 | 27.1 | 2.22
6856 | 369.4 | 177.8 | 574 | 26.2 | 2.78
6857 | 41.7 | 44.4 | 0 | 24.9 | 2.22
6858 | 0 | 0 | 0 | 23.4 | 2.78
6859 | 0 | 0 | 0 | 23.3 | 1.67
6860 | 0 | 0 | 0 | 23.2 | 1.11
6861 | 0 | 0 | 0 | 23.2 | 2.22
6862 | 0 | 0 | 0 | 22.5 | 2.78
6863 | 0 | 0 | 0 | 21.6 | 2.22
6864 | 0 | 0 | 0 | 21.6 | 3.89
6865 | 0 | 0 | 0 | 20.9 | 2.78
6866 | 0 | 0 | 0 | 20.9 | 0
6867 | 0 | 0 | 0 | 20.7 | 0
6868 | 0 | 0 | 0 | 20.6 | 1.67
6869 | 0 | 0 | 0 | 20.1 | 2.22
6870 | 25 | 22.2 | 31 | 20.3 | 2.22
6871 | 241.7 | 88.9 | 460 | 21.1 | 1.67
6872 | 533.3 | 100 | 788.5 | 23.7 | 1.67
6873 | 797.2 | 113.9 | 939.8 | 25.7 | 1.67
6874 | 872.2 | 272.2 | 703.7 | 26.6 | 1.67
6875 | 983.3 | 158.3 | 899 | 27.5 | 1.67
6876 | 883.3 | 230.6 | 711.3 | 27.6 | 3.33
6877 | 663.9 | 291.7 | 436.5 | 27.6 | 2.78
6878 | 630.6 | 247.2 | 527.2 | 28.1 | 3.33
6879 | 555.6 | 122.2 | 788.5 | 28 | 2.78
6880 | 327.8 | 127.8 | 602.2 | 27.6 | 2.78
6881 | 88.9 | 50 | 213.3 | 26.1 | 3.89
6882 | 0 | 0 | 0 | 24.9 | 2.22
6883 | 0 | 0 | 0 | 23.9 | 2.22
6884 | 0 | 0 | 0 | 23.4 | 2.22
6885 | 0 | 0 | 0 | 22.8 | 2.22
6886 | 0 | 0 | 0 | 22.6 | 1.11
6887 | 0 | 0 | 0 | 22.1 | 2.22
6888 | 0 | 0 | 0 | 21.4 | 4.17
6889 | 0 | 0 | 0 | 20.8 | 1.67
6890 | 0 | 0 | 0 | 20.4 | 1.67
6891 | 0 | 0 | 0 | 19.8 | 0
6892 | 0 | 0 | 0 | 20 | 0
6893 | 0 | 0 | 0 | 20 | 1.11
6894 | 36.1 | 25 | 126.3 | 20 | 1.67
6895 | 186.1 | 152.8 | 100.9 | 21.4 | 1.67
6896 | 411.1 | 200 | 385.6 | 23.3 | 1.67
6897 | 375 | 283.3 | 126.5 | 24.6 | 1.67
6898 | 761.1 | 425 | 395.3 | 27.4 | 1.67
6899 | 972.2 | 469.4 | 549.4 | 27.6 | 3.33
6900 | 886.1 | 461.1 | 464.4 | 27.8 | 3.89
6901 | 836.1 | 447.2 | 457.4 | 28.3 | 3.33
6902 | 644.4 | 377.8 | 367.9 | 28 | 2.78
6903 | 375 | 277.8 | 177.6 | 27.5 | 2.78
6904 | 302.8 | 194.4 | 328 | 26.7 | 2.78
6905 | 36.1 | 30.6 | 63.1 | 25.3 | 2.78
6906 | 0 | 0 | 0 | 24.3 | 2.78
6907 | 0 | 0 | 0 | 23.5 | 2.22
6908 | 0 | 0 | 0 | 22 | 1.11
6909 | 0 | 0 | 0 | 21.8 | 1.67
6910 | 0 | 0 | 0 | 21.1 | 1.67
6911 | 0 | 0 | 0 | 20.5 | 2.22
6912 | 0 | 0 | 0 | 20.5 | 4.44
6913 | 0 | 0 | 0 | 20.8 | 1.67
6914 | 0 | 0 | 0 | 21.4 | 2.22
6915 | 0 | 0 | 0 | 21.9 | 2.22
6916 | 0 | 0 | 0 | 21.3 | 1.67
6917 | 0 | 0 | 0 | 21.3 | 2.22
6918 | 25 | 22.2 | 32.1 | 21.4 | 2.22
6919 | 172.2 | 141.7 | 93 | 23.6 | 2.78
6920 | 255.6 | 233.3 | 40.7 | 23.2 | 3.33
6921 | 661.1 | 394.4 | 369 | 24.4 | 2.78
6922 | 780.6 | 511.1 | 317.8 | 26.1 | 2.78
6923 | 661.1 | 505.6 | 170.4 | 26.1 | 3.33
6924 | 311.1 | 291.7 | 21.3 | 25.8 | 2.78
6925 | 425 | 383.3 | 49.1 | 26 | 2.78
6926 | 483.3 | 427.8 | 76.9 | 25.6 | 3.33
6927 | 441.7 | 327.8 | 208.8 | 26.2 | 3.89
6928 | 313.9 | 211.1 | 312.9 | 26.2 | 3.33
6929 | 58.3 | 41.7 | 192.8 | 25.4 | 3.33
6930 | 0 | 0 | 0 | 24.4 | 2.22
6931 | 0 | 0 | 0 | 23.7 | 1.67
6932 | 0 | 0 | 0 | 23.1 | 0
6933 | 0 | 0 | 0 | 22.8 | 2.22
6934 | 0 | 0 | 0 | 22.7 | 0
6935 | 0 | 0 | 0 | 22.1 | 2.78
6936 | 0 | 0 | 0 | 22.1 | 4.72
6937 | 0 | 0 | 0 | 21.9 | 4.44
6938 | 0 | 0 | 0 | 21.6 | 3.33
6939 | 0 | 0 | 0 | 21.9 | 3.33
6940 | 0 | 0 | 0 | 21 | 0
6941 | 0 | 0 | 0 | 20.4 | 3.33
6942 | 30.6 | 27.8 | 32.7 | 20.5 | 2.78
6943 | 283.3 | 155.6 | 391.2 | 22.9 | 2.78
6944 | 502.8 | 216.7 | 526.5 | 23.6 | 3.89
6945 | 738.9 | 255.6 | 671 | 24.2 | 3.89
6946 | 866.7 | 313.9 | 653.8 | 25.7 | 4.44
6947 | 644.4 | 391.7 | 277.7 | 26.4 | 2.78
6948 | 733.3 | 375 | 393.7 | 27.2 | 2.78
6949 | 605.6 | 313.9 | 345 | 28.2 | 3.89
6950 | 677.8 | 322.2 | 493.6 | 27.9 | 3.89
6951 | 575 | 269.4 | 562.3 | 27.2 | 3.33
6952 | 355.6 | 191.7 | 501.7 | 27.1 | 3.33
6953 | 94.4 | 61.1 | 194.3 | 26.5 | 2.78
6954 | 0 | 0 | 0 | 25.5 | 1.67
6955 | 0 | 0 | 0 | 25.1 | 2.22
6956 | 0 | 0 | 0 | 21.5 | 9.44
6957 | 0 | 0 | 0 | 21.4 | 2.78
6958 | 0 | 0 | 0 | 21.5 | 3.33
6959 | 0 | 0 | 0 | 21.2 | 3.33
6960 | 0 | 0 | 0 | 21.2 | 5
6961 | 0 | 0 | 0 | 21.2 | 2.78
6962 | 0 | 0 | 0 | 21.2 | 3.33
6963 | 0 | 0 | 0 | 21.2 | 2.78
6964 | 0 | 0 | 0 | 21.2 | 2.78
6965 | 0 | 0 | 0 | 21.2 | 2.78
6966 | 25 | 11.1 | 166.6 | 21.2 | 1.67
6967 | 77.8 | 61.1 | 51.3 | 21.5 | 2.78
6968 | 402.8 | 247.2 | 287.4 | 23.1 | 2.22
6969 | 847.2 | 250 | 831.7 | 25.1 | 2.22
6970 | 955.6 | 186.1 | 912.7 | 26.2 | 2.78
6971 | 988.9 | 219.4 | 847.6 | 27.9 | 2.78
6972 | 766.7 | 377.8 | 428.4 | 28.6 | 2.78
6973 | 680.6 | 377.8 | 359.1 | 29.6 | 2.78
6974 | 530.6 | 297.2 | 324.9 | 27.8 | 2.22
6975 | 172.2 | 155.6 | 30.8 | 25.6 | 2.22
6976 | 50 | 47.2 | 8.6 | 20.8 | 3.33
6977 | 5.6 | 2.8 | 33.3 | 20.2 | 2.22
6978 | 0 | 0 | 0 | 20.2 | 3.33
6979 | 0 | 0 | 0 | 20.2 | 2.78
6980 | 0 | 0 | 0 | 20.2 | 2.78
6981 | 0 | 0 | 0 | 20 | 2.78
6982 | 0 | 0 | 0 | 20.1 | 0
6983 | 0 | 0 | 0 | 20.2 | 0
6984 | 0 | 0 | 0 | 20.3 | 5.28
6985 | 0 | 0 | 0 | 20.3 | 2.22
6986 | 0 | 0 | 0 | 20.4 | 2.78
6987 | 0 | 0 | 0 | 20.4 | 0
6988 | 0 | 0 | 0 | 20.4 | 0
6989 | 0 | 0 | 0 | 20.4 | 0
6990 | 66.7 | 11.1 | 181.7 | 20.7 | 2.78
6991 | 352.8 | 188.9 | 507.4 | 22.1 | 0
6992 | 336.1 | 308.3 | 51.5 | 22.2 | 0
6993 | 441.7 | 366.7 | 104.8 | 23.7 | 2.65
6994 | 330.6 | 277.8 | 62.8 | 24.5 | 1.67
6995 | 758.3 | 350 | 451.1 | 25.4 | 1.67
6996 | 491.7 | 325 | 184.1 | 27 | 1.11
6997 | 530.6 | 275 | 304 | 27.4 | 2.22
6998 | 722.2 | 144.4 | 807.2 | 27.8 | 2.22
6999 | 400 | 119.4 | 520.3 | 28.2 | 2.22
7000 | 202.8 | 86.1 | 361.2 | 28.1 | 2.22
7001 | 55.6 | 25 | 181.7 | 26.4 | 2.22
7002 | 0 | 0 | 0 | 25 | 1.11
7003 | 0 | 0 | 0 | 23 | 5.56
7004 | 0 | 0 | 0 | 23 | 1.11
7005 | 0 | 0 | 0 | 23 | 3.33
7006 | 0 | 0 | 0 | 22.3 | 3.33
7007 | 0 | 0 | 0 | 21.8 | 4.44
7008 | 0 | 0 | 0 | 21.8 | 5.56
7009 | 0 | 0 | 0 | 21.8 | 3.33
7010 | 0 | 0 | 0 | 21.7 | 2.22
7011 | 0 | 0 | 0 | 21.5 | 1.67
7012 | 0 | 0 | 0 | 21.5 | 1.67
7013 | 0 | 0 | 0 | 21.3 | 1.11
7014 | 50 | 41.7 | 103.7 | 21.4 | 1.67
7015 | 205.6 | 186.1 | 60.5 | 22 | 1.67
7016 | 380.6 | 297.2 | 155.1 | 22.7 | 1.67
7017 | 625 | 450 | 245.3 | 24 | 2.78
7018 | 638.9 | 480.6 | 188.9 | 26.5 | 2.22
7019 | 850 | 411.1 | 486.2 | 26.9 | 1.67
7020 | 638.9 | 358.3 | 310.8 | 26.9 | 1.11
7021 | 925 | 288.9 | 758.9 | 27.7 | 0.56
7022 | 483.3 | 266.7 | 303.7 | 25.2 | 1.67
7023 | 161.1 | 138.9 | 41.4 | 22.4 | 5
7024 | 30.6 | 30.6 | 0 | 22 | 2.78
7025 | 0 | 0 | 0 | 22.1 | 1.11
7026 | 0 | 0 | 0 | 22.4 | 1.11
7027 | 0 | 0 | 0 | 20.9 | 1.11
7028 | 0 | 0 | 0 | 21 | 2.78
7029 | 0 | 0 | 0 | 21.2 | 1.11
7030 | 0 | 0 | 0 | 21.2 | 0
7031 | 0 | 0 | 0 | 21.2 | 1.11
7032 | 0 | 0 | 0 | 21 | 5.83
7033 | 0 | 0 | 0 | 21 | 3.89
7034 | 0 | 0 | 0 | 20.9 | 2.22
7035 | 0 | 0 | 0 | 20.9 | 2.78
7036 | 0 | 0 | 0 | 20.8 | 2.22
7037 | 0 | 0 | 0 | 20.6 | 1.67
7038 | 50 | 38.9 | 141 | 20.7 | 1.67
7039 | 152.8 | 138.9 | 43.5 | 21 | 2.78
7040 | 377.8 | 333.3 | 83.1 | 22.6 | 2.22
7041 | 430.6 | 372.2 | 82 | 22.9 | 3.89
7042 | 583.3 | 444.4 | 166.2 | 24.3 | 2.22
7043 | 613.9 | 441.7 | 191.3 | 25.7 | 3.33
7044 | 897.2 | 416.7 | 533.8 | 26 | 3.33
7045 | 891.7 | 322.2 | 681.4 | 27.2 | 3.89
7046 | 797.2 | 263.9 | 749.9 | 26.9 | 2.22
7047 | 452.8 | 202.8 | 467.2 | 26.7 | 2.22
7048 | 133.3 | 86.1 | 147.8 | 25.5 | 3.89
7049 | 33.3 | 19.4 | 169.2 | 24.4 | 2.78
7050 | 0 | 0 | 0 | 23.7 | 2.22
7051 | 0 | 0 | 0 | 22.9 | 1.67
7052 | 0 | 0 | 0 | 22.5 | 1.67
7053 | 0 | 0 | 0 | 22.4 | 2.22
7054 | 0 | 0 | 0 | 22.4 | 2.78
7055 | 0 | 0 | 0 | 21.7 | 2.78
7056 | 0 | 0 | 0 | 21.8 | 6.11
7057 | 0 | 0 | 0 | 21.8 | 1.67
7058 | 0 | 0 | 0 | 21.4 | 2.78
7059 | 0 | 0 | 0 | 21.3 | 2.78
7060 | 0 | 0 | 0 | 21.2 | 1.67
7061 | 0 | 0 | 0 | 20.8 | 2.22
7062 | 47.2 | 30.6 | 163.1 | 20.8 | 2.22
7063 | 300 | 86.1 | 673.5 | 21.6 | 2.78
7064 | 611.1 | 100 | 875.2 | 24 | 5
7065 | 788.9 | 100 | 939.4 | 24.8 | 5.56
7066 | 961.1 | 166.7 | 953.4 | 25.8 | 5
7067 | 905.6 | 302.8 | 671.5 | 26.4 | 4.44
7068 | 986.1 | 222.2 | 851 | 27.1 | 3.33
7069 | 930.6 | 222.2 | 850.1 | 27.9 | 3.89
7070 | 669.4 | 225 | 626.9 | 27.9 | 3.33
7071 | 600 | 208.3 | 734.8 | 27.7 | 3.89
7072 | 344.4 | 169.4 | 551 | 27.2 | 4.44
7073 | 69.4 | 41.7 | 163.1 | 25.1 | 3.33
7074 | 0 | 0 | 0 | 23.6 | 2.22
7075 | 0 | 0 | 0 | 22.6 | 1.67
7076 | 0 | 0 | 0 | 22.7 | 1.11
7077 | 0 | 0 | 0 | 21.8 | 1.67
7078 | 0 | 0 | 0 | 21.2 | 1.67
7079 | 0 | 0 | 0 | 21.2 | 2.22
7080 | 0 | 0 | 0 | 21.2 | 6.39
7081 | 0 | 0 | 0 | 21.2 | 2.22
7082 | 0 | 0 | 0 | 21 | 2.22
7083 | 0 | 0 | 0 | 20.9 | 1.67
7084 | 0 | 0 | 0 | 20.7 | 1.67
7085 | 0 | 0 | 0 | 20.6 | 1.11
7086 | 25 | 16.7 | 109.9 | 20.6 | 2.22
7087 | 227.8 | 122.2 | 334.2 | 21.8 | 2.22
7088 | 558.3 | 116.7 | 831.9 | 24.1 | 2.78
7089 | 636.1 | 161.1 | 672.2 | 25 | 2.78
7090 | 727.8 | 319.4 | 491.5 | 26.1 | 3.89
7091 | 905.6 | 302.8 | 673.4 | 27.6 | 3.89
7092 | 886.1 | 311.1 | 642.4 | 27.8 | 4.44
7093 | 913.9 | 194.4 | 866 | 26.4 | 3.33
7094 | 777.8 | 211.1 | 802 | 28.1 | 3.89
7095 | 352.8 | 211.1 | 266.8 | 27.9 | 5
7096 | 61.1 | 50 | 35.2 | 26 | 4.44
7097 | 13.9 | 5.6 | 109.9 | 24.8 | 3.89
7098 | 0 | 0 | 0 | 24.1 | 2.78
7099 | 0 | 0 | 0 | 23.8 | 2.22
7100 | 0 | 0 | 0 | 23.1 | 3.89
7101 | 0 | 0 | 0 | 22.1 | 3.89
7102 | 0 | 0 | 0 | 21.2 | 3.89
7103 | 0 | 0 | 0 | 20.4 | 2.78
7104 | 0 | 0 | 0 | 20.2 | 6.67
7105 | 0 | 0 | 0 | 19.8 | 2.78
7106 | 0 | 0 | 0 | 19.6 | 2.22
7107 | 0 | 0 | 0 | 19.7 | 2.78
7108 | 0 | 0 | 0 | 19.5 | 2.78
7109 | 0 | 0 | 0 | 18.8 | 2.22
7110 | 25 | 13.9 | 149.4 | 18.9 | 1.67
7111 | 280.6 | 80.6 | 636.9 | 20.4 | 2.22
7112 | 572.2 | 83.3 | 873.2 | 23 | 3.89
7113 | 788.9 | 91.7 | 938 | 25.1 | 5
7114 | 922.2 | 116.7 | 968.9 | 26.4 | 3.89
7115 | 991.7 | 208.3 | 877.6 | 27.3 | 3.33
7116 | 988.9 | 286.1 | 787.4 | 27.9 | 4.44
7117 | 913.9 | 275 | 771.3 | 27.3 | 4.44
7118 | 705.6 | 280.6 | 603.4 | 27.5 | 4.44
7119 | 497.2 | 297.2 | 378.2 | 27.5 | 3.33
7120 | 319.4 | 236.1 | 265.4 | 26.9 | 3.33
7121 | 69.4 | 66.7 | 37.3 | 25.5 | 2.78
7122 | 0 | 0 | 0 | 23.9 | 0
7123 | 0 | 0 | 0 | 23.7 | 0
7124 | 0 | 0 | 0 | 23.2 | 2.22
7125 | 0 | 0 | 0 | 23.1 | 2.22
7126 | 0 | 0 | 0 | 22.7 | 2.78
7127 | 0 | 0 | 0 | 22 | 2.22
7128 | 0 | 0 | 0 | 21.5 | 6.94
7129 | 0 | 0 | 0 | 21.2 | 2.78
7130 | 0 | 0 | 0 | 20.7 | 2.78
7131 | 0 | 0 | 0 | 20.7 | 2.22
7132 | 0 | 0 | 0 | 20.8 | 1.67
7133 | 0 | 0 | 0 | 20.7 | 1.11
7134 | 19.4 | 13.9 | 76.2 | 20.6 | 2.78
7135 | 127.8 | 116.7 | 35.6 | 21.7 | 2.22
7136 | 166.7 | 161.1 | 10.5 | 23.2 | 1.67
7137 | 358.3 | 327.8 | 43.5 | 23.8 | 2.22
7138 | 708.3 | 619.4 | 107.6 | 25.5 | 1.67
7139 | 591.7 | 538.9 | 59.3 | 25.6 | 2.78
7140 | 455.6 | 436.1 | 21.8 | 26.1 | 2.78
7141 | 547.2 | 452.8 | 114.4 | 26.3 | 2.78
7142 | 522.2 | 430.6 | 130.6 | 26.9 | 3.33
7143 | 569.4 | 433.3 | 258.4 | 26.8 | 3.89
7144 | 305.6 | 250 | 177.9 | 24.5 | 3.33
7145 | 52.8 | 41.7 | 144.8 | 23.1 | 5.56
7146 | 0 | 0 | 0 | 22.2 | 3.33
7147 | 0 | 0 | 0 | 21.4 | 3.89
7148 | 0 | 0 | 0 | 21.1 | 3.33
7149 | 0 | 0 | 0 | 21.2 | 2.22
7150 | 0 | 0 | 0 | 21 | 2.22
7151 | 0 | 0 | 0 | 20.8 | 2.22
7152 | 0 | 0 | 0 | 20.8 | 7.22
7153 | 0 | 0 | 0 | 20.8 | 2.22
7154 | 0 | 0 | 0 | 20.5 | 2.78
7155 | 0 | 0 | 0 | 20.1 | 2.78
7156 | 0 | 0 | 0 | 20.2 | 3.33
7157 | 0 | 0 | 0 | 19.8 | 3.89
7158 | 19.4 | 16.7 | 38.9 | 20.1 | 2.78
7159 | 91.7 | 102.8 | 0 | 20.8 | 2.22
7160 | 341.7 | 288.9 | 100.6 | 22.7 | 2.78
7161 | 550 | 350 | 285.8 | 24 | 2.78
7162 | 636.1 | 469.4 | 202.4 | 26.1 | 3.33
7163 | 1008.3 | 343.1 | 438.4 | 26.7 | 2.22
7164 | 650 | 344.7 | 451.2 | 27.1 | 2.22
7165 | 500 | 350 | 182.2 | 28 | 2.78
7166 | 263.9 | 258.3 | 7.9 | 26.7 | 3.33
7167 | 261.1 | 247.2 | 26.5 | 26.4 | 2.78
7168 | 155.6 | 138.9 | 53.7 | 25.7 | 2.78
7169 | 55.6 | 22.2 | 138.9 | 25.2 | 2.78
7170 | 0 | 0 | 0 | 24.1 | 2.22
7171 | 0 | 0 | 0 | 23.3 | 1.67
7172 | 0 | 0 | 0 | 23.2 | 2.22
7173 | 0 | 0 | 0 | 22.5 | 2.22
7174 | 0 | 0 | 0 | 21.9 | 2.78
7175 | 0 | 0 | 0 | 21.5 | 2.78
7176 | 0 | 0 | 0 | 21.12 | 7.5
7177 | 0 | 0 | 0 | 20.99 | 2.78
7178 | 0 | 0 | 0 | 20.82 | 1.67
7179 | 0 | 0 | 0 | 20.73 | 0
7180 | 0 | 0 | 0 | 20.65 | 2.78
7181 | 0 | 0 | 0 | 20.43 | 2.22
7182 | 33.3 | 22.2 | 133 | 20.52 | 1.67
7183 | 222.2 | 111.1 | 359.9 | 21.41 | 2.78
7184 | 388.9 | 222.2 | 318.9 | 23.09 | 2.78
7185 | 541.7 | 266.7 | 394.3 | 24.28 | 2.78
7186 | 572.2 | 355.6 | 263.9 | 25.49 | 2.78
7187 | 911.1 | 377.8 | 602.7 | 26.4 | 3.33
7188 | 1002.8 | 219.4 | 885.2 | 26.82 | 2.78
7189 | 747.2 | 247.2 | 609.1 | 27.16 | 2.78
7190 | 705.6 | 161.1 | 780.7 | 26.99 | 2.78
7191 | 575 | 130.6 | 850.3 | 26.52 | 2.78
7192 | 336.1 | 88.9 | 711.4 | 25.46 | 2.22
7193 | 38.9 | 16.7 | 133 | 24.44 | 2.78
7194 | 0 | 0 | 0 | 24.6 | 2.22
7195 | 0 | 0 | 0 | 23.5 | 2.22
7196 | 0 | 0 | 0 | 22.8 | 2.22
7197 | 0 | 0 | 0 | 22.1 | 2.22
7198 | 0 | 0 | 0 | 21.6 | 1.67
7199 | 0 | 0 | 0 | 21.1 | 2.22
7200 | 0 | 0 | 0 | 20.9 | 7.78
7201 | 0 | 0 | 0 | 20.6 | 2.22
7202 | 0 | 0 | 0 | 20.3 | 2.22
7203 | 0 | 0 | 0 | 20.1 | 1.67
7204 | 0 | 0 | 0 | 19.8 | 2.78
7205 | 0 | 0 | 0 | 19.1 | 2.22
7206 | 36.1 | 16.7 | 127.2 | 19.1 | 2.22
7207 | 216.7 | 102.8 | 371 | 20.3 | 2.22
7208 | 533.3 | 119.4 | 794.9 | 23.2 | 2.78
7209 | 777.8 | 113.9 | 935.4 | 25.2 | 3.89
7210 | 897.2 | 180.6 | 875.6 | 26.2 | 3.89
7211 | 900 | 294.4 | 686.3 | 26.7 | 3.33
7212 | 758.3 | 294.4 | 525.8 | 26.3 | 2.78
7213 | 833.3 | 225 | 743.3 | 27.4 | 2.78
7214 | 725 | 211.1 | 739.3 | 26.9 | 3.89
7215 | 466.7 | 163.9 | 581.5 | 26.6 | 2.22
7216 | 313.9 | 108.3 | 669.6 | 26.1 | 2.22
7217 | 61.1 | 30.6 | 127.2 | 24.9 | 1.67
7218 | 0 | 0 | 0 | 23.6 | 2.22
7219 | 0 | 0 | 0 | 22.6 | 1.67
7220 | 0 | 0 | 0 | 21.9 | 2.22
7221 | 0 | 0 | 0 | 21.5 | 2.22
7222 | 0 | 0 | 0 | 20.7 | 2.22
7223 | 0 | 0 | 0 | 19.9 | 1.67
7224 | 0 | 0 | 0 | 19.8 | 8.06
7225 | 0 | 0 | 0 | 19.5 | 2.22
7226 | 0 | 0 | 0 | 18.9 | 2.22
7227 | 0 | 0 | 0 | 18.7 | 1.67
7228 | 0 | 0 | 0 | 18.4 | 1.67
7229 | 0 | 0 | 0 | 18.4 | 2.22
7230 | 30.6 | 13.9 | 121.6 | 18.6 | 1.67
7231 | 250 | 72.2 | 582.4 | 20 | 2.78
7232 | 552.8 | 116.7 | 840.9 | 23.4 | 2.78
7233 | 669.4 | 188.9 | 693.6 | 25.8 | 3.89
7234 | 905.6 | 227.8 | 830.6 | 26.3 | 5
7235 | 775 | 313.9 | 524.1 | 27.2 | 4.44
7236 | 741.7 | 319.4 | 479.9 | 27.8 | 5
7237 | 850 | 291.7 | 684.2 | 28.3 | 3.89
7238 | 475 | 286.1 | 272.6 | 29.1 | 3.33
7239 | 338.9 | 238.9 | 192.8 | 27.3 | 2.78
7240 | 69.4 | 66.7 | 9.1 | 26.5 | 2.22
7241 | 5.6 | 5.6 | 0 | 25.6 | 1.67
7242 | 0 | 0 | 0 | 25.2 | 2.78
7243 | 0 | 0 | 0 | 22.6 | 1.67
7244 | 0 | 0 | 0 | 22.5 | 2.22
7245 | 0 | 0 | 0 | 22.5 | 2.22
7246 | 0 | 0 | 0 | 22 | 2.22
7247 | 0 | 0 | 0 | 21.6 | 3.33
7248 | 0 | 0 | 0 | 21.1 | 8.33
7249 | 0 | 0 | 0 | 20.8 | 2.22
7250 | 0 | 0 | 0 | 20.6 | 2.22
7251 | 0 | 0 | 0 | 20.6 | 2.22
7252 | 0 | 0 | 0 | 20.3 | 2.78
7253 | 0 | 0 | 0 | 19.8 | 2.22
7254 | 16.7 | 13.9 | 42.1 | 19.8 | 2.78
7255 | 238.9 | 88.9 | 494.2 | 20.7 | 2.78
7256 | 497.2 | 219.4 | 537.7 | 22.2 | 2.78
7257 | 550 | 338.9 | 305.7 | 23.9 | 2.78
7258 | 708.3 | 397.2 | 382.4 | 23.4 | 3.89
7259 | 800 | 466.7 | 380 | 25.2 | 2.78
7260 | 677.8 | 522.2 | 177.3 | 25.6 | 3.89
7261 | 558.3 | 463.9 | 116.1 | 25.9 | 2.78
7262 | 358.3 | 347.2 | 16.1 | 26.9 | 2.78
7263 | 200 | 202.8 | 0 | 26.2 | 2.78
7264 | 122.2 | 130.6 | 0 | 25.1 | 2.78
7265 | 22.2 | 27.8 | 0 | 23.6 | 2.78
7266 | 0 | 0 | 0 | 23.4 | 2.78
7267 | 0 | 0 | 0 | 22.9 | 2.78
7268 | 0 | 0 | 0 | 21.9 | 3.89
7269 | 0 | 0 | 0 | 21.2 | 2.78
7270 | 0 | 0 | 0 | 20.6 | 2.22
7271 | 0 | 0 | 0 | 20.1 | 2.22
7272 | 0 | 0 | 0 | 20.1 | 8.61
7273 | 0 | 0 | 0 | 20.1 | 3.33
7274 | 0 | 0 | 0 | 20.1 | 3.33
7275 | 0 | 0 | 0 | 19.9 | 2.78
7276 | 0 | 0 | 0 | 19.8 | 0
7277 | 0 | 0 | 0 | 19.6 | 0
7278 | 25 | 19.4 | 86.1 | 19.6 | 0
7279 | 194.4 | 130.6 | 211.7 | 20.5 | 2.78
7280 | 527.8 | 102.8 | 825.9 | 23.6 | 2.78
7281 | 769.4 | 172.2 | 867.7 | 25.1 | 4.44
7282 | 775 | 252.8 | 643.8 | 25.8 | 4.44
7283 | 633.3 | 330.6 | 346.1 | 26.7 | 3.33
7284 | 750 | 319.4 | 492.2 | 27.8 | 2.78
7285 | 694.4 | 372.2 | 397.2 | 26.8 | 3.89
7286 | 513.9 | 275 | 347.1 | 27.5 | 2.78
7287 | 469.4 | 166.7 | 588.4 | 26.5 | 2.78
7288 | 269.4 | 147.2 | 404.9 | 26.4 | 1.67
7289 | 86.1 | 41.7 | 110.5 | 25.7 | 2.78
7290 | 0 | 0 | 0 | 24.9 | 2.22
7291 | 0 | 0 | 0 | 22.8 | 1.67
7292 | 0 | 0 | 0 | 23.2 | 1.67
7293 | 0 | 0 | 0 | 22.2 | 0
7294 | 0 | 0 | 0 | 21.7 | 0
7295 | 0 | 0 | 0 | 21.2 | 0
7296 | 0 | 0 | 0 | 20.7 | 0.28
7297 | 0 | 0 | 0 | 20.2 | 2.22
7298 | 0 | 0 | 0 | 19.6 | 1.67
7299 | 0 | 0 | 0 | 19 | 1.67
7300 | 0 | 0 | 0 | 18.7 | 1.67
7301 | 0 | 0 | 0 | 18.4 | 1.67
7302 | 36.1 | 5.6 | 121.9 | 18.4 | 1.67
7303 | 236.1 | 61.1 | 583 | 20 | 1.67
7304 | 494.4 | 102.8 | 764.1 | 22.5 | 1.11
7305 | 688.9 | 136.1 | 805.7 | 24.8 | 1.67
7306 | 794.4 | 177.8 | 762.5 | 25.2 | 2.22
7307 | 663.9 | 250 | 474.5 | 25.7 | 2.22
7308 | 633.3 | 297.2 | 385.4 | 27.4 | 2.22
7309 | 516.7 | 250 | 329.7 | 27.7 | 1.67
7310 | 305.6 | 213.9 | 133.6 | 27.6 | 1.11
7311 | 205.6 | 144.4 | 119.2 | 27.3 | 1.11
7312 | 177.8 | 116.7 | 203.6 | 26.4 | 1.11
7313 | 50 | 11.1 | 121.9 | 25.1 | 2.22
7314 | 0 | 0 | 0 | 24 | 2.22
7315 | 0 | 0 | 0 | 23.5 | 2.22
7316 | 0 | 0 | 0 | 22.8 | 2.22
7317 | 0 | 0 | 0 | 22 | 2.22
7318 | 0 | 0 | 0 | 21.2 | 2.22
7319 | 0 | 0 | 0 | 20.8 | 2.22
7320 | 0 | 0 | 0 | 20.4 | 0.56
7321 | 0 | 0 | 0 | 20.1 | 2.22
7322 | 0 | 0 | 0 | 19.9 | 2.22
7323 | 0 | 0 | 0 | 20.1 | 2.22
7324 | 0 | 0 | 0 | 20.2 | 2.22
7325 | 0 | 0 | 0 | 20.2 | 2.22
7326 | 38.9 | 2.8 | 116.1 | 20.2 | 2.22
7327 | 236.1 | 33.3 | 679.4 | 21 | 2.22
7328 | 341.7 | 150 | 375.4 | 23.2 | 0
7329 | 555.6 | 233.3 | 471.2 | 24.3 | 3.33
7330 | 700 | 313.9 | 478.9 | 26 | 2.78
7331 | 569.4 | 330.6 | 274.7 | 26.5 | 3.33
7332 | 525 | 383.3 | 162.9 | 26.9 | 2.78
7333 | 802.8 | 277.8 | 651.1 | 26.3 | 2.78
7334 | 633.3 | 219.4 | 605.3 | 21.5 | 2.22
7335 | 380.6 | 202.8 | 348.2 | 22.4 | 3.89
7336 | 30.6 | 8.3 | 74.5 | 20.4 | 0
7337 | 2.8 | 0 | 44.9 | 20.9 | 5.56
7338 | 0 | 0 | 0 | 20.6 | 3.33
7339 | 0 | 0 | 0 | 20.6 | 3.33
7340 | 0 | 0 | 0 | 20.4 | 3.33
7341 | 0 | 0 | 0 | 20.3 | 3.33
7342 | 0 | 0 | 0 | 20.3 | 3.33
7343 | 0 | 0 | 0 | 20 | 3.33
7344 | 0 | 0 | 0 | 19.9 | 0.83
7345 | 0 | 0 | 0 | 19.8 | 3.33
7346 | 0 | 0 | 0 | 19.4 | 3.33
7347 | 0 | 0 | 0 | 19.4 | 3.33
7348 | 0 | 0 | 0 | 19.4 | 3.33
7349 | 0 | 0 | 0 | 19.4 | 3.33
7350 | 55.6 | 11.1 | 110.5 | 19.4 | 3.33
7351 | 191.7 | 58.3 | 449.2 | 20.4 | 3.33
7352 | 450 | 147.2 | 595.3 | 22.5 | 0
7353 | 627.8 | 205.6 | 619.5 | 24.1 | 0
7354 | 730.6 | 280.6 | 559.8 | 25.5 | 3.89
7355 | 797.2 | 283.3 | 592.6 | 26.4 | 2.78
7356 | 813.9 | 216.7 | 688.7 | 26.9 | 3.89
7357 | 655.6 | 216.7 | 546 | 26.9 | 3.33
7358 | 658.3 | 158.3 | 733.6 | 27.4 | 3.89
7359 | 313.9 | 147.2 | 327.7 | 27.4 | 3.33
7360 | 150 | 66.7 | 280.7 | 26.6 | 4.44
7361 | 41.7 | 5.6 | 110.5 | 25.2 | 2.78
7362 | 0 | 0 | 0 | 24.2 | 2.22
7363 | 0 | 0 | 0 | 23.5 | 2.22
7364 | 0 | 0 | 0 | 22.4 | 0
7365 | 0 | 0 | 0 | 21.9 | 0
7366 | 0 | 0 | 0 | 21.4 | 0.56
7367 | 0 | 0 | 0 | 21.4 | 0.56
7368 | 0 | 0 | 0 | 20.6 | 1.11
7369 | 0 | 0 | 0 | 20.4 | 0
7370 | 0 | 0 | 0 | 20.3 | 0
7371 | 0 | 0 | 0 | 20.1 | 0
7372 | 0 | 0 | 0 | 19.7 | 0
7373 | 0 | 0 | 0 | 19.7 | 0
7374 | 19.4 | 2.8 | 104.9 | 19.8 | 0
7375 | 141.7 | 75 | 225.8 | 20.9 | 0
7376 | 438.9 | 180.6 | 509.8 | 22.6 | 0
7377 | 586.1 | 177.8 | 601 | 24.2 | 3.33
7378 | 758.3 | 194.4 | 703.5 | 26 | 2.78
7379 | 852.8 | 202.8 | 751.7 | 26 | 3.89
7380 | 869.4 | 213.9 | 758.1 | 28.6 | 3.33
7381 | 625 | 238.9 | 481.7 | 27.2 | 3.89
7382 | 452.8 | 183.3 | 396.6 | 27.1 | 3.89
7383 | 419.4 | 122.2 | 586.6 | 27.5 | 3.33
7384 | 266.7 | 113.9 | 517.5 | 26.5 | 3.33
7385 | 25 | 2.8 | 104.9 | 25.6 | 3.33
7386 | 0 | 0 | 0 | 22.17 | 3.33
7387 | 0 | 0 | 0 | 21.61 | 3.33
7388 | 0 | 0 | 0 | 21.06 | 3.33
7389 | 0 | 0 | 0 | 20.7 | 1.67
7390 | 0 | 0 | 0 | 20.44 | 2.22
7391 | 0 | 0 | 0 | 20.2 | 2.22
7392 | 0 | 0 | 0 | 22.2 | 1.39
7393 | 0 | 0 | 0 | 22 | 1.67
7394 | 0 | 0 | 0 | 21.6 | 1.67
7395 | 0 | 0 | 0 | 21.5 | 0
7396 | 0 | 0 | 0 | 21.4 | 0
7397 | 0 | 0 | 0 | 21.3 | 0
7398 | 30.6 | 13.9 | 99.5 | 21.2 | 0
7399 | 127.8 | 55.6 | 246 | 21.5 | 0
7400 | 263.9 | 177.8 | 170.6 | 23 | 0
7401 | 438.9 | 269.4 | 250.2 | 24 | 0
7402 | 702.8 | 308.3 | 493.6 | 25.5 | 1.67
7403 | 711.1 | 322.2 | 451 | 25.6 | 2.22
7404 | 716.7 | 336.1 | 441.3 | 26.4 | 3.89
7405 | 755.6 | 261.1 | 618.7 | 26.7 | 2.78
7406 | 511.1 | 155.6 | 525 | 27.2 | 3.89
7407 | 452.8 | 161.1 | 577.8 | 26.8 | 2.78
7408 | 227.8 | 75 | 520.4 | 26.2 | 1.67
7409 | 47.2 | 16.7 | 99.5 | 25.6 | 2.78
7410 | 0 | 0 | 0 | 24.9 | 2.78
7411 | 0 | 0 | 0 | 24.1 | 2.22
7412 | 0 | 0 | 0 | 23.1 | 2.22
7413 | 0 | 0 | 0 | 22.7 | 0
7414 | 0 | 0 | 0 | 22.4 | 0
7415 | 0 | 0 | 0 | 22.9 | 0
7416 | 0 | 0 | 0 | 21.7 | 1.67
7417 | 0 | 0 | 0 | 21.4 | 0
7418 | 0 | 0 | 0 | 21.4 | 0
7419 | 0 | 0 | 0 | 21.2 | 0
7420 | 0 | 0 | 0 | 20.8 | 0
7421 | 0 | 0 | 0 | 20.4 | 0
7422 | 50 | 5.6 | 94.3 | 19.9 | 0
7423 | 241.7 | 25 | 726.7 | 21.6 | 0
7424 | 463.9 | 69.4 | 784.4 | 24.6 | 0
7425 | 575 | 216.7 | 530.8 | 26.5 | 1.67
7426 | 533.3 | 191.7 | 428.8 | 26.4 | 1.67
7427 | 727.8 | 266.7 | 536.3 | 27.4 | 2.22
7428 | 694.4 | 425 | 313.4 | 27.6 | 3.33
7429 | 408.3 | 263.9 | 181.3 | 27.9 | 1.11
7430 | 444.4 | 266.7 | 263.4 | 27.9 | 1.67
7431 | 416.7 | 325 | 182.3 | 27.5 | 2.22
7432 | 244.4 | 122.2 | 418.6 | 27.2 | 1.67
7433 | 27.8 | 11.1 | 94.3 | 26.1 | 1.67
7434 | 0 | 0 | 0 | 25.5 | 1.67
7435 | 0 | 0 | 0 | 24.9 | 1.67
7436 | 0 | 0 | 0 | 24.6 | 1.67
7437 | 0 | 0 | 0 | 22.9 | 1.67
7438 | 0 | 0 | 0 | 22.5 | 1.67
7439 | 0 | 0 | 0 | 21.9 | 1.67
7440 | 0 | 0 | 0 | 21.1 | 1.94
7441 | 0 | 0 | 0 | 21.4 | 0
7442 | 0 | 0 | 0 | 21.4 | 0
7443 | 0 | 0 | 0 | 19.9 | 0
7444 | 0 | 0 | 0 | 19.2 | 0
7445 | 0 | 0 | 0 | 19 | 0
7446 | 30.6 | 5.6 | 89.1 | 19 | 0
7447 | 191.7 | 55.6 | 468.7 | 20.5 | 0
7448 | 344.4 | 144.4 | 399.2 | 22.5 | 0
7449 | 444.4 | 252.8 | 284.8 | 23.8 | 3.33
7450 | 575 | 316.7 | 325.2 | 25.1 | 3.89
7451 | 558.3 | 366.7 | 223.5 | 25.9 | 2.22
7452 | 386.1 | 333.3 | 61.6 | 25.8 | 2.78
7453 | 608.3 | 375 | 293.7 | 25.8 | 2.78
7454 | 441.7 | 288.9 | 227 | 25.9 | 2.78
7455 | 344.4 | 227.8 | 232.9 | 26.6 | 1.67
7456 | 191.7 | 127.8 | 220 | 25.9 | 0
7457 | 19.4 | 5.6 | 89.1 | 24.6 | 2.78
7458 | 0 | 0 | 0 | 23.9 | 1.67
7459 | 0 | 0 | 0 | 23.4 | 1.67
7460 | 0 | 0 | 0 | 23.3 | 1.67
7461 | 0 | 0 | 0 | 23.1 | 1.67
7462 | 0 | 0 | 0 | 22.6 | 1.67
7463 | 0 | 0 | 0 | 22.4 | 1.67
7464 | 0 | 0 | 0 | 22.4 | 2.22
7465 | 0 | 0 | 0 | 22.1 | 0
7466 | 0 | 0 | 0 | 21.9 | 0
7467 | 0 | 0 | 0 | 21.7 | 0
7468 | 0 | 0 | 0 | 21.4 | 0
7469 | 0 | 0 | 0 | 21.1 | 0
7470 | 30.6 | 13.9 | 84.2 | 21.2 | 0
7471 | 211.1 | 80.6 | 452 | 21.7 | 0
7472 | 286.1 | 138.9 | 295 | 22.8 | 1.67
7473 | 283.3 | 180.6 | 153.2 | 23.6 | 3.33
7474 | 336.1 | 200 | 171.8 | 24.2 | 3.33
7475 | 330.6 | 216.7 | 133.2 | 23.9 | 2.78
7476 | 244.4 | 175 | 81.2 | 21.9 | 2.78
7477 | 194.4 | 125 | 87.7 | 22.5 | 3.89
7478 | 316.7 | 233.3 | 124.2 | 23 | 3.89
7479 | 411.1 | 227.8 | 367.3 | 24.1 | 3.33
7480 | 191.7 | 91.7 | 346.2 | 23.2 | 3.33
7481 | 22.2 | 13.9 | 84.2 | 22.2 | 3.33
7482 | 0 | 0 | 0 | 22.17 | 2.78
7483 | 0 | 0 | 0 | 21.61 | 2.22
7484 | 0 | 0 | 0 | 21.06 | 1.11
7485 | 0 | 0 | 0 | 20.7 | 2.78
7486 | 0 | 0 | 0 | 20.44 | 2.78
7487 | 0 | 0 | 0 | 20.2 | 2.78
7488 | 0 | 0 | 0 | 20.9 | 2.5
7489 | 0 | 0 | 0 | 20.7 | 1.67
7490 | 0 | 0 | 0 | 20.6 | 1.67
7491 | 0 | 0 | 0 | 20.7 | 1.67
7492 | 0 | 0 | 0 | 20.7 | 1.67
7493 | 0 | 0 | 0 | 20.5 | 1.67
7494 | 38.9 | 11.1 | 79.4 | 20.6 | 1.67
7495 | 136.1 | 61.1 | 261 | 20.7 | 1.67
7496 | 191.7 | 122.2 | 139.6 | 21.5 | 1.67
7497 | 394.4 | 258.3 | 203.5 | 22.8 | 2.78
7498 | 544.4 | 322.2 | 281.3 | 24.6 | 2.78
7499 | 800 | 269.4 | 622.2 | 25.7 | 2.78
7500 | 672.2 | 227.8 | 521.2 | 26.3 | 3.33
7501 | 658.3 | 238.9 | 531 | 26.4 | 3.89
7502 | 525 | 227.8 | 444.5 | 22.3 | 2.78
7503 | 194.4 | 130.6 | 128.5 | 22.8 | 2.78
7504 | 119.4 | 55.6 | 222.3 | 22.8 | 2.22
7505 | 22.2 | 5.6 | 79.4 | 22.2 | 2.78
7506 | 0 | 0 | 0 | 21.6 | 1.11
7507 | 0 | 0 | 0 | 21.2 | 0
7508 | 0 | 0 | 0 | 21.2 | 0
7509 | 0 | 0 | 0 | 21 | 2.22
7510 | 0 | 0 | 0 | 20.9 | 2.78
7511 | 0 | 0 | 0 | 20.3 | 2.5
7512 | 0 | 0 | 0 | 20.3 | 2.78
7513 | 0 | 0 | 0 | 20 | 2.5
7514 | 0 | 0 | 0 | 19.8 | 2.5
7515 | 0 | 0 | 0 | 19.4 | 2.5
7516 | 0 | 0 | 0 | 18.8 | 2.5
7517 | 0 | 0 | 0 | 18.3 | 2.5
7518 | 27.8 | 11.1 | 74.7 | 18.3 | 2.5
7519 | 263.9 | 36.1 | 719 | 18.4 | 2.5
7520 | 502.8 | 52.8 | 889.9 | 21 | 2.78
7521 | 711.1 | 52.8 | 958.8 | 23.4 | 2.78
7522 | 838.9 | 63.9 | 983.9 | 25 | 2.78
7523 | 897.2 | 69.4 | 973.5 | 26.1 | 3.33
7524 | 925 | 177.8 | 878.8 | 26.5 | 2.78
7525 | 725 | 205.6 | 659.5 | 26.9 | 2.22
7526 | 536.1 | 169.4 | 550 | 26.6 | 2.78
7527 | 475 | 94.4 | 768.1 | 25.9 | 4.44
7528 | 252.8 | 55.6 | 690 | 25.6 | 2.78
7529 | 44.4 | 13.9 | 74.7 | 23.5 | 2.78
7530 | 0 | 0 | 0 | 22.17 | 1.11
7531 | 0 | 0 | 0 | 21.61 | 1.67
7532 | 0 | 0 | 0 | 21.06 | 1.67
7533 | 0 | 0 | 0 | 20.7 | 2.78
7534 | 0 | 0 | 0 | 20.44 | 2.22
7535 | 0 | 0 | 0 | 20.2 | 2.22
7536 | 0 | 0 | 0 | 19.1 | 3.06
7537 | 0 | 0 | 0 | 18.9 | 2.22
7538 | 0 | 0 | 0 | 18.9 | 2.22
7539 | 0 | 0 | 0 | 18.7 | 2.22
7540 | 0 | 0 | 0 | 18.4 | 2.22
7541 | 0 | 0 | 0 | 17.9 | 2.22
7542 | 22.2 | 8.3 | 70.2 | 18 | 2.22
7543 | 169.4 | 72.2 | 341.9 | 18.5 | 2.22
7544 | 375 | 172.2 | 410.7 | 20.2 | 3.33
7545 | 658.3 | 186.1 | 710.5 | 23.4 | 2.78
7546 | 822.2 | 150 | 855.8 | 25 | 3.33
7547 | 913.9 | 122.2 | 933.6 | 26.4 | 3.33
7548 | 863.9 | 116.7 | 881.1 | 27.2 | 3.33
7549 | 747.2 | 122.2 | 795.7 | 27.7 | 3.33
7550 | 577.8 | 108.3 | 706.4 | 27.9 | 2.78
7551 | 452.8 | 75 | 765.2 | 26.7 | 2.78
7552 | 266.7 | 44.4 | 717.2 | 26.1 | 1.11
7553 | 52.8 | 5.6 | 70.2 | 24.9 | 2.78
7554 | 0 | 0 | 0 | 23.8 | 1.11
7555 | 0 | 0 | 0 | 22.7 | 0
7556 | 0 | 0 | 0 | 21.6 | 1.11
7557 | 0 | 0 | 0 | 21.2 | 2.22
7558 | 0 | 0 | 0 | 20.6 | 1.11
7559 | 0 | 0 | 0 | 20.1 | 0
7560 | 0 | 0 | 0 | 20.1 | 3.33
7561 | 0 | 0 | 0 | 19.6 | 1.11
7562 | 0 | 0 | 0 | 19.4 | 1.67
7563 | 0 | 0 | 0 | 19.4 | 1.67
7564 | 0 | 0 | 0 | 19.1 | 1.67
7565 | 0 | 0 | 0 | 19.2 | 1.67
7566 | 41.7 | 16.7 | 65.9 | 19.2 | 1.67
7567 | 227.8 | 94.4 | 471.3 | 20.1 | 1.67
7568 | 430.6 | 177.8 | 513.9 | 22.3 | 2.78
7569 | 633.3 | 200 | 654 | 25.8 | 2.78
7570 | 591.7 | 222.2 | 471.7 | 26.6 | 5.56
7571 | 538.9 | 272.2 | 315.3 | 26.8 | 5
7572 | 775 | 269.4 | 597.8 | 26.3 | 3.33
7573 | 586.1 | 277.8 | 393.6 | 26 | 2.78
7574 | 597.2 | 244.4 | 532.4 | 26 | 2.78
7575 | 427.8 | 130.6 | 604.2 | 25 | 4.44
7576 | 244.4 | 63.9 | 638.2 | 24.1 | 4.44
7577 | 13.9 | 16.7 | 0 | 20.3 | 5.56
7578 | 0 | 0 | 0 | 20.2 | 3.89
7579 | 0 | 0 | 0 | 20.2 | 2.22
7580 | 0 | 0 | 0 | 20.2 | 2.22
7581 | 0 | 0 | 0 | 20.2 | 2.78
7582 | 0 | 0 | 0 | 20.1 | 2.22
7583 | 0 | 0 | 0 | 19.9 | 2.78
7584 | 0 | 0 | 0 | 19.7 | 3.61
7585 | 0 | 0 | 0 | 19.7 | 2.78
7586 | 0 | 0 | 0 | 19.9 | 2.78
7587 | 0 | 0 | 0 | 19.9 | 2.78
7588 | 0 | 0 | 0 | 19.9 | 2.78
7589 | 0 | 0 | 0 | 19.9 | 2.22
7590 | 5.6 | 11.1 | 0 | 19.9 | 2.78
7591 | 75 | 50 | 88.8 | 20 | 2.78
7592 | 316.7 | 211.1 | 215.3 | 21.4 | 5
7593 | 394.4 | 277.8 | 176.6 | 22 | 5.56
7594 | 411.1 | 322.2 | 113.8 | 22.4 | 5.56
7595 | 411.1 | 272.2 | 164.7 | 21.4 | 6.11
7596 | 608.3 | 402.8 | 243.7 | 22.7 | 5.56
7597 | 455.6 | 322.2 | 170.7 | 23.5 | 5.56
7598 | 419.4 | 272.2 | 222.9 | 23.9 | 5.56
7599 | 277.8 | 152.8 | 255 | 23.6 | 6.11
7600 | 86.1 | 30.6 | 197.4 | 21.3 | 5.56
7601 | 11.1 | 11.1 | 0 | 21.1 | 5.56
7602 | 0 | 0 | 0 | 22.17 | 4.44
7603 | 0 | 0 | 0 | 21.61 | 5.56
7604 | 0 | 0 | 0 | 21.06 | 5.56
7605 | 0 | 0 | 0 | 20.7 | 5.56
7606 | 0 | 0 | 0 | 20.44 | 2.78
7607 | 0 | 0 | 0 | 20.2 | 4.44
7608 | 0 | 0 | 0 | 19.4 | 3.89
7609 | 0 | 0 | 0 | 19.4 | 3.33
7610 | 0 | 0 | 0 | 19.2 | 4.44
7611 | 0 | 0 | 0 | 19.2 | 3.33
7612 | 0 | 0 | 0 | 19.3 | 3.33
7613 | 0 | 0 | 0 | 19.5 | 3.89
7614 | 0 | 8.3 | 0 | 19.5 | 5.56
7615 | 36.1 | 22.2 | 49.6 | 19.5 | 5.56
7616 | 61.1 | 36.1 | 51.2 | 19.4 | 5
7617 | 130.6 | 83.3 | 71.7 | 20.3 | 3.33
7618 | 488.9 | 355.6 | 171.2 | 20.8 | 5.56
7619 | 286.1 | 194.4 | 109 | 21.8 | 5.56
7620 | 155.6 | 150 | 6.6 | 22.3 | 5.56
7621 | 216.7 | 191.7 | 32.1 | 22 | 5.56
7622 | 269.4 | 222.2 | 71.7 | 20.8 | 5.56
7623 | 227.8 | 152.8 | 153.5 | 20.8 | 4.44
7624 | 25 | 30.6 | 0 | 20.7 | 3.89
7625 | 25 | 8.3 | 57.8 | 20.3 | 4.44
7626 | 0 | 0 | 0 | 19.9 | 4.44
7627 | 0 | 0 | 0 | 19.8 | 2.78
7628 | 0 | 0 | 0 | 19.8 | 3.33
7629 | 0 | 0 | 0 | 19.8 | 4.44
7630 | 0 | 0 | 0 | 19.7 | 5.56
7631 | 0 | 0 | 0 | 19.5 | 3.89
7632 | 0 | 0 | 0 | 19.4 | 4.17
7633 | 0 | 0 | 0 | 19.3 | 3.33
7634 | 0 | 0 | 0 | 19.2 | 3.89
7635 | 0 | 0 | 0 | 19 | 3.33
7636 | 0 | 0 | 0 | 19 | 3.89
7637 | 0 | 0 | 0 | 18.8 | 3.89
7638 | 5.6 | 8.3 | 0 | 18.8 | 3.89
7639 | 38.9 | 30.6 | 29.9 | 19.2 | 3.89
7640 | 94.4 | 58.3 | 74.2 | 20.2 | 3.33
7641 | 222.2 | 188.9 | 50.8 | 20.7 | 3.33
7642 | 322.2 | 272.2 | 64.4 | 20.7 | 2.78
7643 | 158.3 | 133.3 | 29.8 | 20.5 | 4.44
7644 | 327.8 | 269.4 | 69.5 | 22.6 | 5.56
7645 | 366.7 | 322.2 | 57.2 | 22.9 | 3.89
7646 | 275 | 241.7 | 50.8 | 23.1 | 3.89
7647 | 141.7 | 113.9 | 57.1 | 22.5 | 3.33
7648 | 58.3 | 41.7 | 59.8 | 21.2 | 5
7649 | 11.1 | 5.6 | 54 | 20.9 | 3.33
7650 | 0 | 0 | 0 | 20.9 | 3.33
7651 | 0 | 0 | 0 | 20.7 | 3.89
7652 | 0 | 0 | 0 | 20.4 | 5.56
7653 | 0 | 0 | 0 | 20.1 | 3.89
7654 | 0 | 0 | 0 | 20 | 2.78
7655 | 0 | 0 | 0 | 19.8 | 2.78
7656 | 0 | 0 | 0 | 19.1 | 4.44
7657 | 0 | 0 | 0 | 19.8 | 3.33
7658 | 0 | 0 | 0 | 19.8 | 3.33
7659 | 0 | 0 | 0 | 19.9 | 3.89
7660 | 0 | 0 | 0 | 19.9 | 3.33
7661 | 0 | 0 | 0 | 19.9 | 3.33
7662 | 5.6 | 11.1 | 0 | 19.9 | 2.78
7663 | 77.8 | 47.2 | 110.2 | 20 | 3.33
7664 | 119.4 | 88.9 | 63 | 20.3 | 3.33
7665 | 241.7 | 211.1 | 46.7 | 20.5 | 3.33
7666 | 458.3 | 355.6 | 132.6 | 21.4 | 3.33
7667 | 330.6 | 294.4 | 43.1 | 22.5 | 3.89
7668 | 286.1 | 247.2 | 46.5 | 23.2 | 3.89
7669 | 308.3 | 258.3 | 64.5 | 24 | 3.33
7670 | 286.1 | 252.8 | 50.9 | 24.3 | 4.44
7671 | 141.7 | 113.9 | 57.3 | 24.2 | 5.56
7672 | 50 | 25 | 90.1 | 23.2 | 3.89
7673 | 25 | 8.3 | 50.4 | 21.8 | 4.44
7674 | 0 | 0 | 0 | 21.3 | 3.33
7675 | 0 | 0 | 0 | 21.2 | 4.44
7676 | 0 | 0 | 0 | 21.2 | 4.44
7677 | 0 | 0 | 0 | 20.8 | 5
7678 | 0 | 0 | 0 | 20.8 | 3.33
7679 | 0 | 0 | 0 | 20.8 | 3.89
7680 | 0 | 0 | 0 | 20.5 | 4.72
7681 | 0 | 0 | 0 | 20.4 | 4.44
7682 | 0 | 0 | 0 | 20.4 | 3.89
7683 | 0 | 0 | 0 | 20.4 | 4.44
7684 | 0 | 0 | 0 | 20.4 | 5.56
7685 | 0 | 0 | 0 | 20.2 | 4.44
7686 | 5.6 | 11.1 | 0 | 20.2 | 3.89
7687 | 61.1 | 38.9 | 80.5 | 20.3 | 3.89
7688 | 169.4 | 122.2 | 97.7 | 20.2 | 3.89
7689 | 302.8 | 216.7 | 131.9 | 20.6 | 3.89
7690 | 230.6 | 202.8 | 35.9 | 20.8 | 4.44
7691 | 250 | 211.1 | 46.6 | 22.4 | 4.44
7692 | 461.1 | 272.2 | 226.2 | 23.3 | 5
7693 | 486.1 | 247.2 | 309.1 | 24 | 5
7694 | 236.1 | 188.9 | 72.3 | 24.4 | 5
7695 | 80.6 | 52.8 | 57.4 | 22 | 5
7696 | 152.8 | 100 | 191.2 | 21.5 | 3.89
7697 | 36.1 | 16.7 | 47 | 21.1 | 3.89
7698 | 0 | 0 | 0 | 21.1 | 3.33
7699 | 0 | 0 | 0 | 21.1 | 1.11
7700 | 0 | 0 | 0 | 21.1 | 0
7701 | 0 | 0 | 0 | 21 | 0
7702 | 0 | 0 | 0 | 20.6 | 0
7703 | 0 | 0 | 0 | 20.2 | 0
7704 | 0 | 0 | 0 | 19.7 | 5
7705 | 0 | 0 | 0 | 19.4 | 0
7706 | 0 | 0 | 0 | 19.1 | 0
7707 | 0 | 0 | 0 | 19.2 | 0
7708 | 0 | 0 | 0 | 19.2 | 0
7709 | 0 | 0 | 0 | 18.8 | 0
7710 | 36.1 | 8.3 | 43.7 | 18.8 | 0
7711 | 147.2 | 55.6 | 333.6 | 19 | 0
7712 | 338.9 | 158.3 | 374.6 | 20.4 | 0
7713 | 352.8 | 191.7 | 247.4 | 22.9 | 0
7714 | 575 | 375 | 259.4 | 24.3 | 0
7715 | 513.9 | 422.2 | 110.1 | 24.9 | 3.33
7716 | 486.1 | 336.1 | 180.1 | 25.1 | 1.67
7717 | 336.1 | 266.7 | 90.1 | 25.2 | 0
7718 | 300 | 247.2 | 81 | 25.4 | 2.22
7719 | 133.3 | 97.2 | 74.9 | 25.4 | 0
7720 | 83.3 | 61.1 | 80.9 | 24.7 | 0
7721 | 8.3 | 16.7 | 0 | 24 | 0
7722 | 0 | 0 | 0 | 22.8 | 0
7723 | 0 | 0 | 0 | 22.1 | 0
7724 | 0 | 0 | 0 | 21 | 3.89
7725 | 0 | 0 | 0 | 21 | 2.78
7726 | 0 | 0 | 0 | 21 | 2.78
7727 | 0 | 0 | 0 | 20.8 | 2.22
7728 | 0 | 0 | 0 | 20.6 | 5.28
7729 | 0 | 0 | 0 | 20.6 | 0
7730 | 0 | 0 | 0 | 20.6 | 0
7731 | 0 | 0 | 0 | 20.4 | 0
7732 | 0 | 0 | 0 | 20 | 0
7733 | 0 | 0 | 0 | 19.8 | 0
7734 | 11.1 | 11.1 | 0 | 19.8 | 0
7735 | 50 | 30.6 | 71.1 | 19.9 | 0
7736 | 116.7 | 63.9 | 109.8 | 20.6 | 0
7737 | 350 | 252.8 | 149.7 | 22.9 | 0
7738 | 730.6 | 361.1 | 480.4 | 24 | 2.78
7739 | 661.1 | 319.4 | 411.2 | 24.8 | 2.78
7740 | 825 | 86.1 | 889.3 | 24.9 | 3.89
7741 | 630.6 | 88.9 | 704.4 | 26.3 | 3.33
7742 | 533.3 | 38.9 | 761.3 | 27 | 3.33
7743 | 455.6 | 88.9 | 763.1 | 26.8 | 2.78
7744 | 244.4 | 94.4 | 548.5 | 26.8 | 2.78
7745 | 52.8 | 41.7 | 40.6 | 25.4 | 2.78
7746 | 0 | 0 | 0 | 24.1 | 0
7747 | 0 | 0 | 0 | 23.3 | 0
7748 | 0 | 0 | 0 | 22.7 | 0
7749 | 0 | 0 | 0 | 22.3 | 0
7750 | 0 | 0 | 0 | 21.9 | 0
7751 | 0 | 0 | 0 | 21.4 | 0
7752 | 0 | 0 | 0 | 21.3 | 5.56
7753 | 0 | 0 | 0 | 20.5 | 0
7754 | 0 | 0 | 0 | 20.4 | 0
7755 | 0 | 0 | 0 | 20.4 | 0
7756 | 0 | 0 | 0 | 20.4 | 0
7757 | 0 | 0 | 0 | 20.4 | 0
7758 | 2.8 | 12.4 | 82.5 | 20.4 | 0
7759 | 105.6 | 72.8 | 292.3 | 20.7 | 0
7760 | 291.7 | 149.9 | 394.6 | 21.6 | 1.67
7761 | 319.4 | 198.4 | 455.7 | 22.6 | 2.78
7762 | 408.3 | 242.3 | 501.7 | 23.2 | 0.56
7763 | 336.1 | 242.3 | 471.4 | 23.5 | 0.56
7764 | 375 | 248.4 | 474.6 | 23.1 | 1.11
7765 | 30.6 | 235 | 443.2 | 22.3 | 2.78
7766 | 61.1 | 214 | 402.1 | 21.2 | 2.78
7767 | 72.2 | 153.8 | 388.1 | 21.1 | 1.11
7768 | 44.4 | 76.6 | 328.7 | 21.2 | 0
7769 | 2.8 | 15 | 65.3 | 21.4 | 0
7770 | 0 | 0 | 0 | 21.4 | 0
7771 | 0 | 0 | 0 | 21.4 | 0
7772 | 0 | 0 | 0 | 21.4 | 0
7773 | 0 | 0 | 0 | 21.4 | 0
7774 | 0 | 0 | 0 | 21 | 0
7775 | 0 | 0 | 0 | 20.9 | 0
7776 | 0 | 0 | 0 | 20.9 | 5.83
7777 | 0 | 0 | 0 | 20.2 | 0
7778 | 0 | 0 | 0 | 19.8 | 2.78
7779 | 0 | 0 | 0 | 19.3 | 2.78
7780 | 0 | 0 | 0 | 19.3 | 2.22
7781 | 0 | 0 | 0 | 19.4 | 0
7782 | 5.6 | 22.2 | 0 | 19.1 | 0
7783 | 144.4 | 136.1 | 30.7 | 19.7 | 0
7784 | 500 | 263.9 | 494.5 | 22 | 0
7785 | 563.9 | 202.8 | 558.9 | 22.7 | 1.67
7786 | 797.2 | 113.9 | 892.9 | 24 | 2.78
7787 | 841.7 | 119.4 | 873.3 | 25.5 | 2.78
7788 | 811.1 | 138.9 | 812.9 | 26.1 | 1.11
7789 | 747.2 | 175 | 747.7 | 26.1 | 3.89
7790 | 613.9 | 200 | 640.6 | 25.5 | 2.78
7791 | 391.7 | 150 | 506.1 | 25 | 2.22
7792 | 200 | 86.1 | 420.1 | 24.7 | 2.22
7793 | 19.4 | 25 | 0 | 22.5 | 1.67
7794 | 0 | 0 | 0 | 21.5 | 1.11
7795 | 0 | 0 | 0 | 20.6 | 0
7796 | 0 | 0 | 0 | 20.3 | 1.11
7797 | 0 | 0 | 0 | 20 | 0
7798 | 0 | 0 | 0 | 19.5 | 0
7799 | 0 | 0 | 0 | 19.4 | 0
7800 | 0 | 0 | 0 | 19.3 | 6.11
7801 | 0 | 0 | 0 | 19.3 | 1.11
7802 | 0 | 0 | 0 | 19.3 | 1.11
7803 | 0 | 0 | 0 | 19.4 | 1.11
7804 | 0 | 0 | 0 | 19.4 | 1.11
7805 | 0 | 0 | 0 | 19.4 | 1.11
7806 | 13.9 | 22.2 | 0 | 19.4 | 1.67
7807 | 94.4 | 111.1 | 0 | 19.5 | 0
7808 | 313.9 | 325 | 0 | 20.6 | 1.11
7809 | 480.6 | 383.3 | 150.9 | 21.7 | 1.11
7810 | 605.6 | 327.8 | 363.8 | 24.3 | 2.78
7811 | 647.2 | 294.4 | 427.6 | 25.1 | 3.89
7812 | 677.8 | 308.3 | 447.8 | 26.2 | 2.78
7813 | 525 | 286.1 | 312.9 | 26 | 2.22
7814 | 491.7 | 238.9 | 392.2 | 25.5 | 2.78
7815 | 411.1 | 155.6 | 536.8 | 26 | 2.22
7816 | 147.2 | 102.8 | 164.7 | 25 | 2.78
7817 | 16.7 | 33.3 | 0 | 23.1 | 2.22
7818 | 0 | 0 | 0 | 22 | 2.22
7819 | 0 | 0 | 0 | 21.4 | 1.67
7820 | 0 | 0 | 0 | 20.9 | 3.89
7821 | 0 | 0 | 0 | 20.6 | 0
7822 | 0 | 0 | 0 | 20.5 | 2.22
7823 | 0 | 0 | 0 | 20.5 | 2.22
7824 | 0 | 0 | 0 | 20 | 6.39
7825 | 0 | 0 | 0 | 19.9 | 1.67
7826 | 0 | 0 | 0 | 19.9 | 2.22
7827 | 0 | 0 | 0 | 19.9 | 2.22
7828 | 0 | 0 | 0 | 19.9 | 2.22
7829 | 0 | 0 | 0 | 19.9 | 2.22
7830 | 16.7 | 22.2 | 0 | 20 | 1.11
7831 | 119.4 | 122.2 | 0 | 20.5 | 1.11
7832 | 335.9 | 233.3 | 394.6 | 22.1 | 1.67
7833 | 495.3 | 288.9 | 455.7 | 22.6 | 2.78
7834 | 502.8 | 363.9 | 182.3 | 23.7 | 1.67
7835 | 480.6 | 366.7 | 138.3 | 24.7 | 2.78
7836 | 475 | 300 | 212.6 | 26.7 | 2.22
7837 | 655.6 | 247.2 | 536.1 | 25.9 | 2.78
7838 | 352.8 | 247.2 | 164.2 | 26.5 | 2.22
7839 | 358.3 | 147.2 | 444.7 | 26.6 | 3.33
7840 | 191.7 | 66.7 | 465 | 25.6 | 3.89
7841 | 22.2 | 16.7 | 30 | 23.3 | 2.22
7842 | 0 | 0 | 0 | 22.2 | 2.22
7843 | 0 | 0 | 0 | 21.4 | 2.22
7844 | 0 | 0 | 0 | 20.9 | 2.22
7845 | 0 | 0 | 0 | 20.4 | 2.22
7846 | 0 | 0 | 0 | 20.5 | 2.22
7847 | 0 | 0 | 0 | 20.2 | 2.78
7848 | 0 | 0 | 0 | 20.1 | 6.67
7849 | 0 | 0 | 0 | 19.8 | 2.22
7850 | 0 | 0 | 0 | 19.4 | 2.22
7851 | 0 | 0 | 0 | 19.4 | 2.22
7852 | 0 | 0 | 0 | 19.1 | 2.22
7853 | 0 | 0 | 0 | 18.3 | 2.22
7854 | 5.6 | 13.9 | 0 | 18.3 | 0
7855 | 102.8 | 100 | 10.4 | 18.7 | 2.22
7856 | 405.6 | 225 | 381.4 | 19.7 | 2.22
7857 | 613.9 | 183.3 | 671.4 | 22.7 | 2.22
7858 | 777.8 | 155.6 | 818.7 | 25.2 | 1.67
7859 | 841.7 | 158.3 | 831.8 | 25.7 | 1.67
7860 | 850 | 161.1 | 838.6 | 25.4 | 2.22
7861 | 777.8 | 161.1 | 811.4 | 26.7 | 2.22
7862 | 600 | 166.7 | 675.7 | 26.8 | 1.67
7863 | 375 | 158.3 | 457.7 | 26.5 | 2.78
7864 | 230.6 | 108.3 | 456.6 | 25.6 | 1.67
7865 | 30.6 | 25 | 27.7 | 22.7 | 2.22
7866 | 0 | 0 | 0 | 20.9 | 2.22
7867 | 0 | 0 | 0 | 20 | 2.22
7868 | 0 | 0 | 0 | 19.3 | 2.22
7869 | 0 | 0 | 0 | 19.2 | 0
7870 | 0 | 0 | 0 | 18.8 | 0
7871 | 0 | 0 | 0 | 18 | 0
7872 | 0 | 0 | 0 | 18 | 6.94
7873 | 0 | 0 | 0 | 18 | 0
7874 | 0 | 0 | 0 | 18 | 0
7875 | 0 | 0 | 0 | 17.2 | 0
7876 | 0 | 0 | 0 | 17.3 | 0
7877 | 0 | 0 | 0 | 17.2 | 0
7878 | 11.1 | 13.9 | 0 | 17.2 | 0
7879 | 211.1 | 50 | 604.2 | 17.3 | 0
7880 | 447.2 | 69.4 | 800.3 | 20.6 | 0
7881 | 644.4 | 83.3 | 877 | 23.7 | 1.11
7882 | 783.3 | 122.2 | 871.7 | 26.9 | 2.78
7883 | 847.2 | 150 | 850.5 | 27.1 | 3.89
7884 | 850 | 130.6 | 877.6 | 27.7 | 2.78
7885 | 791.7 | 133.3 | 868 | 27.4 | 2.78
7886 | 663.9 | 133.3 | 829.2 | 27.3 | 3.33
7887 | 458.3 | 105.6 | 747.3 | 27.3 | 2.78
7888 | 236.1 | 75 | 604.2 | 26.7 | 2.22
7889 | 47.2 | 22.2 | 25.6 | 23.7 | 2.22
7890 | 0 | 0 | 0 | 21.7 | 1.67
7891 | 0 | 0 | 0 | 20.4 | 1.67
7892 | 0 | 0 | 0 | 19.7 | 1.67
7893 | 0 | 0 | 0 | 19.7 | 1.67
7894 | 0 | 0 | 0 | 19.1 | 1.11
7895 | 0 | 0 | 0 | 18.7 | 1.11
7896 | 0 | 0 | 0 | 18.2 | 7.22
7897 | 0 | 0 | 0 | 17.5 | 1.11
7898 | 0 | 0 | 0 | 17.7 | 1.11
7899 | 0 | 0 | 0 | 18 | 2.22
7900 | 0 | 0 | 0 | 18.5 | 2.22
7901 | 0 | 0 | 0 | 18.8 | 2.22
7902 | 11.1 | 13.9 | 0 | 18.8 | 1.11
7903 | 158.3 | 105.6 | 198.7 | 18.8 | 2.78
7904 | 441.7 | 116.7 | 690.3 | 20.1 | 2.22
7905 | 605.6 | 136.1 | 735.4 | 23.3 | 2.22
7906 | 747.2 | 163.9 | 770.8 | 24.9 | 2.78
7907 | 816.7 | 194.4 | 760.5 | 25.8 | 2.78
7908 | 763.9 | 252.8 | 624.7 | 26.5 | 2.78
7909 | 547.2 | 272.2 | 363.4 | 27 | 2.22
7910 | 597.2 | 227.8 | 578.7 | 26.9 | 2.22
7911 | 475 | 252.8 | 472 | 25.4 | 1.67
7912 | 91.7 | 75 | 62.7 | 25.2 | 1.67
7913 | 5.6 | 8.3 | 0 | 22.6 | 2.22
7914 | 0 | 0 | 0 | 21.7 | 1.11
7915 | 0 | 0 | 0 | 21.6 | 0.56
7916 | 0 | 0 | 0 | 20.4 | 0
7917 | 0 | 0 | 0 | 19.5 | 0
7918 | 0 | 0 | 0 | 19.5 | 1.11
7919 | 0 | 0 | 0 | 18.9 | 2.78
7920 | 0 | 0 | 0 | 18.4 | 7.5
7921 | 0 | 0 | 0 | 18.3 | 2.78
7922 | 0 | 0 | 0 | 18 | 2.78
7923 | 0 | 0 | 0 | 18.2 | 2.78
7924 | 0 | 0 | 0 | 17.9 | 2.78
7925 | 0 | 0 | 0 | 17.9 | 2.78
7926 | 11.1 | 13.9 | 0 | 17.4 | 2.78
7927 | 169.4 | 83.3 | 325.4 | 18.3 | 2.22
7928 | 416.7 | 105.6 | 662.5 | 21.1 | 2.22
7929 | 613.9 | 122.2 | 771.9 | 23.4 | 2.22
7930 | 755.6 | 138.9 | 816.5 | 25.2 | 1.67
7931 | 825 | 152.8 | 823.3 | 25.8 | 2.22
7932 | 833.3 | 166.7 | 816.5 | 26.3 | 2.78
7933 | 716.7 | 197.2 | 687.7 | 26.2 | 1.67
7934 | 486.1 | 202.8 | 444.8 | 26.7 | 2.78
7935 | 402.8 | 213.9 | 402.2 | 26.2 | 2.78
7936 | 127.8 | 113.9 | 52.5 | 25.2 | 2.22
7937 | 19.4 | 25 | 0 | 24 | 2.78
7938 | 0 | 0 | 0 | 22.4 | 1.11
7939 | 0 | 0 | 0 | 21.7 | 1.11
7940 | 0 | 0 | 0 | 20.1 | 1.67
7941 | 0 | 0 | 0 | 19.2 | 2.78
7942 | 0 | 0 | 0 | 18.8 | 3.33
7943 | 0 | 0 | 0 | 18.3 | 2.22
7944 | 0 | 0 | 0 | 18.3 | 7.78
7945 | 0 | 0 | 0 | 18.3 | 2.78
7946 | 0 | 0 | 0 | 18.4 | 1.11
7947 | 0 | 0 | 0 | 17.8 | 1.67
7948 | 0 | 0 | 0 | 17.2 | 2.22
7949 | 0 | 0 | 0 | 17.2 | 2.22
7950 | 11.1 | 22.2 | 0 | 17.6 | 2.22
7951 | 197.2 | 194.4 | 10.5 | 18.8 | 2.78
7952 | 291.7 | 205.6 | 183.8 | 21.4 | 2.78
7953 | 672.2 | 127.8 | 856.6 | 22.8 | 2.78
7954 | 805.6 | 130.6 | 895.5 | 24.1 | 4.44
7955 | 750 | 230.6 | 637.4 | 25.2 | 4.44
7956 | 794.4 | 275 | 637.4 | 25.3 | 3.89
7957 | 611.1 | 272.2 | 449.6 | 26.2 | 2.22
7958 | 688.9 | 397.2 | 458.9 | 26.2 | 2.22
7959 | 405.6 | 188.9 | 462.5 | 25.1 | 3.89
7960 | 205.6 | 100 | 400.3 | 25.1 | 4.44
7961 | 22.2 | 30.6 | 0 | 23.1 | 3.89
7962 | 0 | 0 | 0 | 21.5 | 2.22
7963 | 0 | 0 | 0 | 20.6 | 2.22
7964 | 0 | 0 | 0 | 19.9 | 2.22
7965 | 0 | 0 | 0 | 19.4 | 2.78
7966 | 0 | 0 | 0 | 19.4 | 2.78
7967 | 0 | 0 | 0 | 19.6 | 2.78
7968 | 0 | 0 | 0 | 19.3 | 8.06
7969 | 0 | 0 | 0 | 18.7 | 2.78
7970 | 0 | 0 | 0 | 18.8 | 2.78
7971 | 0 | 0 | 0 | 18.7 | 2.78
7972 | 0 | 0 | 0 | 18.7 | 2.78
7973 | 0 | 0 | 0 | 18.7 | 1.67
7974 | 22.2 | 25 | 0 | 18.7 | 2.78
7975 | 161.1 | 152.8 | 31.7 | 18.7 | 2.78
7976 | 377.8 | 277.8 | 214 | 19.7 | 2.78
7977 | 594.4 | 236.1 | 564.9 | 21.9 | 3.33
7978 | 777.8 | 280.6 | 660.9 | 23.9 | 2.78
7979 | 833.3 | 297.2 | 659 | 24.5 | 2.22
7980 | 763.9 | 286.1 | 587.3 | 25.7 | 2.22
7981 | 763.9 | 286.1 | 635 | 26.3 | 2.22
7982 | 575 | 244.4 | 521.1 | 26.2 | 0
7983 | 363.9 | 172.2 | 410.2 | 26.1 | 2.78
7984 | 152.8 | 91.7 | 232.6 | 25.2 | 2.22
7985 | 5.6 | 16.7 | 0 | 22.6 | 2.22
7986 | 0 | 0 | 0 | 21.3 | 2.22
7987 | 0 | 0 | 0 | 20.4 | 0
7988 | 0 | 0 | 0 | 19.6 | 0
7989 | 0 | 0 | 0 | 19.1 | 0
7990 | 0 | 0 | 0 | 18.6 | 0
7991 | 0 | 0 | 0 | 18.6 | 0
7992 | 0 | 0 | 0 | 18.1 | 8.33
7993 | 0 | 0 | 0 | 18.1 | 1.11
7994 | 0 | 0 | 0 | 18.1 | 1.11
7995 | 0 | 0 | 0 | 17.6 | 1.11
7996 | 0 | 0 | 0 | 17.2 | 2.22
7997 | 0 | 0 | 0 | 17.1 | 2.22
7998 | 33.3 | 12.4 | 82.5 | 17.1 | 2.22
7999 | 213.9 | 72.8 | 292.3 | 18.3 | 1.67
8000 | 455.6 | 149.9 | 394.6 | 20.4 | 1.67
8001 | 663.9 | 198.4 | 455.7 | 21.8 | 2.22
8002 | 786.1 | 242.3 | 501.7 | 23.3 | 2.78
8003 | 836.1 | 242.3 | 471.4 | 24.8 | 3.33
8004 | 802.8 | 248.4 | 474.6 | 25.6 | 2.22
8005 | 755.6 | 235 | 443.2 | 25.8 | 2.22
8006 | 522.2 | 214 | 402.1 | 25.7 | 2.22
8007 | 305.6 | 153.8 | 388.1 | 25.8 | 2.22
8008 | 180.6 | 76.6 | 328.7 | 24.8 | 2.22
8009 | 11.1 | 15 | 65.3 | 22.3 | 2.22
8010 | 0 | 0 | 0 | 21 | 0
8011 | 0 | 0 | 0 | 20 | 0
8012 | 0 | 0 | 0 | 19.3 | 0
8013 | 0 | 0 | 0 | 19.5 | 0
8014 | 0 | 0 | 0 | 19.7 | 0
8015 | 0 | 0 | 0 | 19.9 | 1.67
8016 | 0 | 0 | 0 | 20 | 0.28
8017 | 0 | 0 | 0 | 19.7 | 2.22
8018 | 0 | 0 | 0 | 18.8 | 2.22
8019 | 0 | 0 | 0 | 18 | 2.22
8020 | 0 | 0 | 0 | 17.5 | 1.67
8021 | 0 | 0 | 0 | 17.6 | 1.67
8022 | 16.8 | 8.3 | 8.2 | 18 | 1.67
8023 | 169 | 72.2 | 379 | 19.6 | 2.22
8024 | 368.6 | 147.2 | 612.9 | 19.9 | 2.78
8025 | 163.9 | 177.8 | 0 | 21.3 | 3.33
8026 | 352.8 | 341.7 | 14.8 | 22.1 | 3.89
8027 | 713.9 | 441.7 | 335.8 | 23.9 | 3.33
8028 | 488.9 | 305.6 | 226.1 | 23.2 | 3.33
8029 | 563.9 | 450 | 151.9 | 24 | 3.33
8030 | 341.7 | 288.9 | 83.5 | 24.3 | 2.78
8031 | 313.9 | 233.3 | 173.2 | 23.5 | 2.78
8032 | 216.7 | 97.2 | 457.5 | 23.1 | 2.78
8033 | 11.1 | 13.9 | 0 | 22.6 | 2.78
8034 | 0 | 0 | 0 | 22.3 | 2.78
8035 | 0 | 0 | 0 | 21.3 | 3.33
8036 | 0 | 0 | 0 | 19.9 | 3.89
8037 | 0 | 0 | 0 | 19.2 | 2.78
8038 | 0 | 0 | 0 | 18.1 | 1.94
8039 | 0 | 0 | 0 | 18.1 | 2.22
8040 | 0 | 0 | 0 | 18.2 | 0.56
8041 | 0 | 0 | 0 | 18.3 | 1.67
8042 | 0 | 0 | 0 | 18 | 2.22
8043 | 0 | 0 | 0 | 18.1 | 2.22
8044 | 0 | 0 | 0 | 17.7 | 2.22
8045 | 0 | 0 | 0 | 17.7 | 1.67
8046 | 8.3 | 0 | 16.4 | 18 | 2.22
8047 | 63.9 | 58.3 | 21.3 | 18.7 | 2.22
8048 | 102.8 | 111.1 | 0 | 20 | 2.22
8049 | 152.8 | 155.6 | 0 | 20.5 | 2.78
8050 | 327.8 | 344.4 | 0 | 23.2 | 3.89
8051 | 275 | 275 | 0 | 24.5 | 5.56
8052 | 594.4 | 483.3 | 137.3 | 23.6 | 5.56
8053 | 591.7 | 427.8 | 219 | 25.5 | 3.89
8054 | 386.1 | 297.2 | 140.9 | 25.9 | 4.44
8055 | 147.2 | 152.8 | 0 | 24.3 | 4.44
8056 | 66.7 | 55.6 | 42.7 | 22.1 | 3.33
8057 | 5.6 | 2.8 | 16.4 | 21.4 | 2.78
8058 | 0 | 0 | 0 | 20.8 | 2.78
8059 | 0 | 0 | 0 | 20.5 | 2.22
8060 | 0 | 0 | 0 | 20.1 | 2.78
8061 | 0 | 0 | 0 | 19.8 | 3.33
8062 | 0 | 0 | 0 | 19.5 | 4.44
8063 | 0 | 0 | 0 | 19.3 | 2.78
8064 | 0 | 0 | 0 | 19.2 | 0.83
8065 | 0 | 0 | 0 | 18.7 | 2.5
8066 | 0 | 0 | 0 | 18.5 | 2.78
8067 | 0 | 0 | 0 | 18.3 | 2.5
8068 | 0 | 0 | 0 | 18.3 | 2.5
8069 | 0 | 0 | 0 | 18.3 | 1.67
8070 | 5.6 | 13.9 | 0 | 18.3 | 2.22
8071 | 61.1 | 75 | 0 | 18.7 | 1.67
8072 | 177.8 | 136.8 | 612.9 | 19.3 | 2.78
8073 | 438.9 | 222.2 | 344.1 | 20.5 | 2.78
8074 | 388.9 | 350 | 52 | 21.5 | 3.33
8075 | 711.1 | 416.7 | 364.4 | 21.6 | 3.33
8076 | 563.9 | 466.7 | 120.3 | 23 | 2.78
8077 | 680.6 | 322.2 | 479.5 | 25 | 2.78
8078 | 591.7 | 269.4 | 511.8 | 24.1 | 2.78
8079 | 416.7 | 197.2 | 473.7 | 23.8 | 2.78
8080 | 227.8 | 91.7 | 524.5 | 23.8 | 2.78
8081 | 22.2 | 13.9 | 15.2 | 21.5 | 2.78
8082 | 0 | 0 | 0 | 20 | 2.22
8083 | 0 | 0 | 0 | 18.4 | 2.22
8084 | 0 | 0 | 0 | 17.6 | 2.22
8085 | 0 | 0 | 0 | 17 | 2.22
8086 | 0 | 0 | 0 | 16.6 | 2.22
8087 | 0 | 0 | 0 | 16.4 | 2.22
8088 | 0 | 0 | 0 | 16.1 | 1.11
8089 | 0 | 0 | 0 | 15.2 | 1.94
8090 | 0 | 0 | 0 | 14.9 | 1.67
8091 | 0 | 0 | 0 | 14.9 | 2.78
8092 | 0 | 0 | 0 | 14.8 | 2.22
8093 | 0 | 0 | 0 | 14.4 | 2.78
8094 | 19.4 | 2.8 | 14.2 | 14.4 | 2.78
8095 | 227.8 | 50 | 687 | 15.9 | 1.67
8096 | 458.3 | 77.8 | 823.1 | 19 | 3.06
8097 | 608.3 | 147.2 | 733.6 | 20.5 | 4.44
8098 | 777.8 | 116.7 | 886.1 | 23.2 | 5.56
8099 | 847.2 | 127.8 | 891.6 | 24.2 | 5
8100 | 850 | 111.1 | 915.7 | 24.7 | 5
8101 | 766.7 | 108.3 | 882.4 | 25.8 | 3.89
8102 | 644.4 | 88.9 | 883.8 | 25.8 | 4.44
8103 | 452.8 | 77.8 | 811.1 | 25.4 | 3.33
8104 | 241.7 | 63.9 | 687 | 24.4 | 3.33
8105 | 38.9 | 16.7 | 14.2 | 21.6 | 3.89
8106 | 0 | 0 | 0 | 19.5 | 2.78
8107 | 0 | 0 | 0 | 20.3 | 2.5
8108 | 0 | 0 | 0 | 17.1 | 2.5
8109 | 0 | 0 | 0 | 16.7 | 2.78
8110 | 0 | 0 | 0 | 16.4 | 2.78
8111 | 0 | 0 | 0 | 15.9 | 2.22
8112 | 0 | 0 | 0 | 15.8 | 1.39
8113 | 0 | 0 | 0 | 15.3 | 2.22
8114 | 0 | 0 | 0 | 14.9 | 2.78
8115 | 0 | 0 | 0 | 15.1 | 1.94
8116 | 0 | 0 | 0 | 15 | 2.22
8117 | 0 | 0 | 0 | 14.9 | 2.78
8118 | 30.6 | 8.3 | 13.2 | 14.8 | 2.78
8119 | 225 | 111.1 | 441.3 | 16 | 2.78
8120 | 400 | 163.9 | 511.6 | 18.7 | 3.33
8121 | 647.2 | 119.4 | 841 | 21.8 | 2.78
8122 | 694.4 | 133.3 | 753.1 | 23.6 | 2.78
8123 | 825 | 138.9 | 851.4 | 24.8 | 2.78
8124 | 791.7 | 150 | 796.3 | 26 | 2.78
8125 | 705.6 | 238.9 | 626.4 | 25.1 | 3.33
8126 | 519.4 | 186.1 | 531.1 | 24.7 | 2.78
8127 | 422.2 | 133.3 | 626 | 25.3 | 3.33
8128 | 194.4 | 69.4 | 484.3 | 24.4 | 3.61
8129 | 16.7 | 11.1 | 13.2 | 22.2 | 2.78
8130 | 0 | 0 | 0 | 20.6 | 2.22
8131 | 0 | 0 | 0 | 19.6 | 1.67
8132 | 0 | 0 | 0 | 19.5 | 1.67
8133 | 0 | 0 | 0 | 18.5 | 2.22
8134 | 0 | 0 | 0 | 18.5 | 1.67
8135 | 0 | 0 | 0 | 18.5 | 2.22
8136 | 0 | 0 | 0 | 18.5 | 1.67
8137 | 0 | 0 | 0 | 18.5 | 3.33
8138 | 0 | 0 | 0 | 18 | 2.78
8139 | 0 | 0 | 0 | 17.5 | 1.67
8140 | 0 | 0 | 0 | 17.7 | 2.78
8141 | 0 | 0 | 0 | 17.7 | 2.22
8142 | 5.6 | 2.8 | 12.3 | 17.7 | 2.78
8143 | 58.3 | 52.8 | 21.6 | 18 | 2.22
8144 | 180.6 | 191.7 | 0 | 17.8 | 2.78
8145 | 447.2 | 363.9 | 133 | 19.1 | 2.78
8146 | 594.4 | 300 | 395.8 | 22.1 | 3.33
8147 | 769.4 | 213.9 | 690.3 | 24.2 | 2.78
8148 | 519.4 | 216.7 | 376.2 | 26 | 2.22
8149 | 547.2 | 205.6 | 459.2 | 26 | 2.78
8150 | 597.2 | 133.3 | 740.2 | 25.9 | 2.22
8151 | 438.9 | 113.9 | 705.4 | 25.5 | 2.78
8152 | 172.2 | 55.6 | 453.1 | 25.6 | 1.11
8153 | 33.3 | 0 | 12.3 | 23.1 | 1.11
8154 | 0 | 0 | 0 | 21.1 | 2.78
8155 | 0 | 0 | 0 | 19.6 | 2.22
8156 | 0 | 0 | 0 | 18.5 | 2.22
8157 | 0 | 0 | 0 | 17.3 | 2.22
8158 | 0 | 0 | 0 | 16.2 | 2.22
8159 | 0 | 0 | 0 | 15.7 | 2.5
8160 | 0 | 0 | 0 | 15 | 1.94
8161 | 0 | 0 | 0 | 14.7 | 2.22
8162 | 0 | 0 | 0 | 14.9 | 1.67
8163 | 0 | 0 | 0 | 14 | 3.33
8164 | 0 | 0 | 0 | 13.7 | 2.22
8165 | 0 | 0 | 0 | 13.1 | 2.78
8166 | 16.7 | 13.9 | 11.5 | 12.8 | 1.67
8167 | 216.7 | 69.4 | 573.2 | 13 | 0.83
8168 | 483.3 | 63.9 | 886.1 | 16.5 | 2.5
8169 | 652.8 | 77.8 | 918.8 | 20 | 2.78
8170 | 766.7 | 77.8 | 927.1 | 22.4 | 2.78
8171 | 825 | 77.8 | 929.7 | 24.4 | 3.06
8172 | 825 | 77.8 | 929.7 | 25.2 | 2.78
8173 | 752.8 | 77.8 | 908.4 | 26.1 | 2.22
8174 | 616.7 | 77.8 | 861.1 | 26.3 | 2.78
8175 | 441.7 | 86.1 | 773 | 25.8 | 2.78
8176 | 222.2 | 61.1 | 627.2 | 24.1 | 3.89
8177 | 38.9 | 0 | 11.5 | 22.6 | 3.89
8178 | 0 | 0 | 0 | 21.4 | 1.94
8179 | 0 | 0 | 0 | 19.5 | 1.67
8180 | 0 | 0 | 0 | 19.4 | 1.67
8181 | 0 | 0 | 0 | 19.3 | 1.67
8182 | 0 | 0 | 0 | 18.7 | 1.11
8183 | 0 | 0 | 0 | 17.7 | 1.67
8184 | 0 | 0 | 0 | 17.4 | 2.22
8185 | 0 | 0 | 0 | 17.2 | 1.11
8186 | 0 | 0 | 0 | 17.3 | 1.11
8187 | 0 | 0 | 0 | 17.3 | 2.22
8188 | 0 | 0 | 0 | 17.3 | 2.22
8189 | 0 | 0 | 0 | 17.2 | 2.22
8190 | 16.7 | 5.6 | 10.8 | 17.1 | 2.22
8191 | 147.2 | 83.3 | 249.3 | 18.4 | 1.11
8192 | 450 | 236.1 | 465.7 | 21.9 | 1.11
8193 | 694.4 | 261.1 | 693.3 | 23.9 | 2.22
8194 | 719.4 | 177.8 | 729.8 | 25.5 | 3.33
8195 | 794.4 | 88.9 | 878.8 | 26.1 | 3.89
8196 | 800 | 100 | 871.9 | 26.2 | 5.56
8197 | 769.4 | 186.1 | 786 | 27 | 5.56
8198 | 433.3 | 238.9 | 311.1 | 26 | 5
8199 | 294.4 | 188.9 | 229.8 | 25 | 4.44
8200 | 172.2 | 83.3 | 346.8 | 23.3 | 4.17
8201 | 25 | 11.1 | 10.8 | 22.7 | 2.22
8202 | 0 | 0 | 0 | 21.7 | 1.67
8203 | 0 | 0 | 0 | 21.1 | 1.94
8204 | 0 | 0 | 0 | 20.9 | 1.39
8205 | 0 | 0 | 0 | 20.4 | 2.22
8206 | 0 | 0 | 0 | 19.8 | 2.22
8207 | 0 | 0 | 0 | 19.5 | 1.94
8208 | 0 | 0 | 0 | 19 | 2.5
8209 | 0 | 0 | 0 | 18.7 | 1.67
8210 | 0 | 0 | 0 | 18.8 | 1.39
8211 | 0 | 0 | 0 | 18.6 | 2.22
8212 | 0 | 0 | 0 | 17.7 | 2.22
8213 | 0 | 0 | 0 | 17.2 | 2.22
8214 | 16.7 | 27.8 | 0 | 17.2 | 1.11
8215 | 183.3 | 79.6 | 379 | 17.9 | 2.22
8216 | 452.8 | 105.6 | 757.1 | 19.9 | 3.33
8217 | 591.7 | 111.1 | 769.8 | 22.6 | 2.78
8218 | 727.8 | 111.1 | 831.8 | 25 | 2.78
8219 | 813.9 | 100 | 890.2 | 26 | 2.78
8220 | 888.9 | 169.4 | 897.1 | 27 | 2.22
8221 | 750 | 286.1 | 625.7 | 26.6 | 1.67
8222 | 541.7 | 300 | 387.1 | 27.6 | 1.39
8223 | 455.6 | 127.8 | 714.7 | 27.2 | 1.67
8224 | 133.3 | 63.9 | 271.5 | 26.2 | 2.78
8225 | 8.3 | 5.6 | 10.2 | 23.6 | 3.61
8226 | 0 | 0 | 0 | 22.1 | 2.22
8227 | 0 | 0 | 0 | 21.1 | 1.67
8228 | 0 | 0 | 0 | 20.8 | 2.78
8229 | 0 | 0 | 0 | 19.8 | 2.22
8230 | 0 | 0 | 0 | 19.8 | 2.22
8231 | 0 | 0 | 0 | 19.7 | 3.61
8232 | 0 | 0 | 0 | 19.7 | 2.78
8233 | 0 | 0 | 0 | 19.8 | 2.78
8234 | 0 | 0 | 0 | 19.8 | 2.78
8235 | 0 | 0 | 0 | 19.3 | 2.78
8236 | 0 | 0 | 0 | 19.1 | 1.67
8237 | 0 | 0 | 0 | 18.5 | 2.22
8238 | 44.4 | 10.4 | 8.2 | 18.6 | 1.11
8239 | 150 | 79.6 | 379 | 19.3 | 1.67
8240 | 377.8 | 144.4 | 509.4 | 22.4 | 3.33
8241 | 622.2 | 108.3 | 824.1 | 23.4 | 1.94
8242 | 727.8 | 105.6 | 840.2 | 25.6 | 1.67
8243 | 802.8 | 77.8 | 904.9 | 27.1 | 3.61
8244 | 805.6 | 77.8 | 908.4 | 28.2 | 3.61
8245 | 741.7 | 127.8 | 828.9 | 28.1 | 3.06
8246 | 608.3 | 198.3 | 523.8 | 26.5 | 2.78
8247 | 216.7 | 88.9 | 279 | 26.1 | 2.78
8248 | 108.3 | 66.7 | 163.2 | 26.5 | 2.78
8249 | 25 | 5.6 | 9.6 | 23.8 | 3.89
8250 | 0 | 0 | 0 | 22.1 | 2.22
8251 | 0 | 0 | 0 | 21.1 | 1.94
8252 | 0 | 0 | 0 | 20.7 | 1.94
8253 | 0 | 0 | 0 | 20.3 | 2.78
8254 | 0 | 0 | 0 | 19.7 | 2.78
8255 | 0 | 0 | 0 | 19.5 | 2.78
8256 | 0 | 0 | 0 | 19.2 | 3.06
8257 | 0 | 0 | 0 | 19.2 | 1.67
8258 | 0 | 0 | 0 | 19.5 | 2.22
8259 | 0 | 0 | 0 | 19 | 2.22
8260 | 0 | 0 | 0 | 18.8 | 2.22
8261 | 0 | 0 | 0 | 18.8 | 3.33
8262 | 11.1 | 11.1 | 0 | 18.7 | 2.78
8263 | 86.1 | 100 | 0 | 18.8 | 2.22
8264 | 322.2 | 197.2 | 273.2 | 21.1 | 3.89
8265 | 525 | 247.2 | 445.9 | 23.4 | 3.61
8266 | 719.4 | 216.7 | 679.5 | 25 | 3.89
8267 | 711.1 | 194.4 | 645.5 | 26.2 | 3.89
8268 | 736.1 | 269.4 | 583 | 27.1 | 4.44
8269 | 488.9 | 225 | 356.7 | 27.1 | 2.78
8270 | 530.6 | 180.6 | 561.9 | 26.7 | 2.78
8271 | 444.4 | 108.3 | 734.7 | 27.4 | 2.78
8272 | 222.2 | 66.7 | 610.3 | 26.9 | 2.78
8273 | 22.2 | 5.6 | 9.1 | 24.3 | 2.78
8274 | 0 | 0 | 0 | 22.1 | 1.11
8275 | 0 | 0 | 0 | 20.9 | 1.67
8276 | 0 | 0 | 0 | 20.2 | 1.67
8277 | 0 | 0 | 0 | 20.1 | 1.67
8278 | 0 | 0 | 0 | 19.9 | 2.78
8279 | 0 | 0 | 0 | 20.1 | 2.22
8280 | 0 | 0 | 0 | 19.9 | 3.33
8281 | 0 | 0 | 0 | 19.6 | 2.22
8282 | 0 | 0 | 0 | 19.3 | 1.67
8283 | 0 | 0 | 0 | 19.1 | 1.67
8284 | 0 | 0 | 0 | 18.9 | 1.67
8285 | 0 | 0 | 0 | 18.8 | 0.56
8286 | 16.8 | 11.1 | 8.2 | 18.8 | 1.67
8287 | 169 | 63.9 | 379 | 19.2 | 1.67
8288 | 368.6 | 113.9 | 612.9 | 22.1 | 2.22
8289 | 602.8 | 80.6 | 839.1 | 24.6 | 2.78
8290 | 722.2 | 86.1 | 860.4 | 26.4 | 2.78
8291 | 777.8 | 100 | 847.4 | 28.7 | 2.22
8292 | 777.8 | 138.9 | 798.8 | 29 | 2.78
8293 | 730.6 | 147.2 | 789.1 | 29.4 | 1.67
8294 | 619.4 | 144.4 | 763.2 | 29.3 | 2.78
8295 | 472.2 | 105.6 | 802.3 | 29.5 | 2.22
8296 | 230.6 | 58.3 | 676.8 | 26.6 | 2.22
8297 | 8.3 | 5.6 | 8.7 | 24.8 | 2.22
8298 | 0 | 0 | 0 | 23 | 1.67
8299 | 0 | 0 | 0 | 22 | 2.22
8300 | 0 | 0 | 0 | 21.6 | 2.22
8301 | 0 | 0 | 0 | 20.6 | 3.33
8302 | 0 | 0 | 0 | 20 | 2.5
8303 | 0 | 0 | 0 | 19.8 | 3.06
8304 | 0 | 0 | 0 | 19.2 | 3.61
8305 | 0 | 0 | 0 | 19.4 | 1.67
8306 | 0 | 0 | 0 | 19.1 | 2.22
8307 | 0 | 0 | 0 | 19.2 | 2.22
8308 | 0 | 0 | 0 | 19.2 | 1.67
8309 | 0 | 0 | 0 | 19.4 | 3.06
8310 | 2.8 | 2.8 | 0 | 19.5 | 3.89
8311 | 83.3 | 63.9 | 76.5 | 19.5 | 2.78
8312 | 416.7 | 100 | 693.6 | 21.3 | 3.33
8313 | 611.1 | 80.6 | 853.2 | 23.5 | 3.89
8314 | 741.7 | 86.1 | 887.4 | 25.8 | 3.89
8315 | 791.7 | 83.3 | 886.3 | 26.6 | 3.89
8316 | 791.7 | 91.7 | 875.9 | 27.8 | 2.78
8317 | 730.6 | 102.8 | 849.8 | 28.6 | 2.78
8318 | 602.8 | 111.1 | 790.7 | 28.5 | 2.78
8319 | 438.9 | 116.7 | 705.8 | 27.5 | 2.78
8320 | 261.1 | 108.3 | 601.2 | 27.1 | 3.33
8321 | 30.6 | 25 | 8.3 | 25.2 | 2.22
8322 | 0 | 0 | 0 | 22.8 | 1.67
8323 | 0 | 0 | 0 | 21.8 | 1.67
8324 | 0 | 0 | 0 | 20.6 | 2.22
8325 | 0 | 0 | 0 | 19.8 | 2.22
8326 | 0 | 0 | 0 | 19 | 1.67
8327 | 0 | 0 | 0 | 18.5 | 1.67
8328 | 0 | 0 | 0 | 17.96 | 3.89
8329 | 0 | 0 | 0 | 17.69 | 1.11
8330 | 0 | 0 | 0 | 17.47 | 1.11
8331 | 0 | 0 | 0 | 17.27 | 1.11
8332 | 0 | 0 | 0 | 17.06 | 1.67
8333 | 0 | 0 | 0 | 16.9 | 1.67
8334 | 27.8 | 27.8 | 0 | 16.89 | 2.78
8335 | 241.7 | 100 | 558.2 | 17.59 | 2.22
8336 | 430.6 | 138.9 | 639.4 | 19.66 | 1.67
8337 | 613.9 | 122.2 | 791.2 | 21.92 | 2.22
8338 | 676.9 | 186.2 | 689.9 | 23.97 | 3.33
8339 | 739.8 | 205.7 | 663.2 | 25.27 | 3.33
8340 | 719.2 | 226.8 | 656.3 | 25.74 | 2.78
8341 | 744.4 | 161.1 | 790.2 | 26.27 | 2.78
8342 | 550 | 236.1 | 505.1 | 26.25 | 3.89
8343 | 297.2 | 272.2 | 54.8 | 25.87 | 2.78
8344 | 144.4 | 150 | 0 | 24.95 | 2.78
8345 | 16.7 | 16.7 | 0 | 23.18 | 3.06
8346 | 0 | 0 | 0 | 22 | 2.5
8347 | 0 | 0 | 0 | 20.9 | 2.22
8348 | 0 | 0 | 0 | 20.4 | 2.22
8349 | 0 | 0 | 0 | 19.3 | 3.06
8350 | 0 | 0 | 0 | 18.8 | 1.94
8351 | 0 | 0 | 0 | 18 | 1.11
8352 | 0 | 0 | 0 | 17.6 | 4.17
8353 | 0 | 0 | 0 | 18 | 1.67
8354 | 0 | 0 | 0 | 18 | 3.33
8355 | 0 | 0 | 0 | 17.7 | 2.22
8356 | 0 | 0 | 0 | 17.7 | 1.67
8357 | 0 | 0 | 0 | 17.8 | 2.22
8358 | 19.4 | 13.9 | 7.7 | 16.7 | 1.67
8359 | 230.6 | 97.2 | 525.9 | 17 | 1.11
8360 | 397.2 | 108.3 | 633.8 | 19.4 | 3.06
8361 | 644.4 | 75 | 917 | 23.2 | 3.33
8362 | 758.3 | 77.8 | 922.4 | 25.8 | 3.33
8363 | 819.4 | 83.3 | 922.1 | 27.1 | 3.89
8364 | 783.3 | 100 | 856 | 28.2 | 3.89
8365 | 741.7 | 80.6 | 896.1 | 28.9 | 3.89
8366 | 518.9 | 198.3 | 523.8 | 28.7 | 3.33
8367 | 365.7 | 144 | 489.5 | 28.1 | 3.06
8368 | 180.1 | 79.7 | 415.4 | 27 | 3.89
8369 | 22.1 | 11.5 | 8.5 | 24.4 | 3.33
8370 | 0 | 0 | 0 | 22.1 | 2.78
8371 | 0 | 0 | 0 | 20.1 | 2.22
8372 | 0 | 0 | 0 | 19.3 | 2.22
8373 | 0 | 0 | 0 | 18.9 | 1.94
8374 | 0 | 0 | 0 | 18.1 | 2.22
8375 | 0 | 0 | 0 | 17.7 | 2.22
8376 | 0 | 0 | 0 | 16.9 | 4.44
8377 | 0 | 0 | 0 | 16.4 | 2.22
8378 | 0 | 0 | 0 | 16.5 | 1.67
8379 | 0 | 0 | 0 | 16.4 | 2.78
8380 | 0 | 0 | 0 | 16.4 | 3.33
8381 | 0 | 0 | 0 | 15.4 | 3.61
8382 | 27.8 | 19.4 | 7.5 | 15.6 | 2.22
8383 | 244.4 | 58.3 | 690.1 | 17.6 | 2.22
8384 | 472.2 | 83.3 | 853.7 | 19.8 | 3.06
8385 | 636.1 | 113.9 | 841.4 | 22.3 | 3.61
8386 | 758.3 | 125 | 858.8 | 24.7 | 3.33
8387 | 783.3 | 130.6 | 818.1 | 25.7 | 3.89
8388 | 808.3 | 108.3 | 877.3 | 26.5 | 4.44
8389 | 755.6 | 100 | 889 | 26.9 | 3.89
8390 | 602.8 | 88.9 | 827.9 | 27 | 2.78
8391 | 427.8 | 75 | 774.4 | 26.6 | 2.78
8392 | 222.2 | 44.4 | 690.1 | 25.5 | 2.78
8393 | 33.3 | 16.7 | 7.5 | 23 | 2.78
8394 | 0 | 0 | 0 | 20.4 | 3.33
8395 | 0 | 0 | 0 | 19 | 1.67
8396 | 0 | 0 | 0 | 17.8 | 2.22
8397 | 0 | 0 | 0 | 17.5 | 2.22
8398 | 0 | 0 | 0 | 17.2 | 2.22
8399 | 0 | 0 | 0 | 16.5 | 2.78
8400 | 0 | 0 | 0 | 15.8 | 4.72
8401 | 0 | 0 | 0 | 15 | 1.67
8402 | 0 | 0 | 0 | 14.5 | 1.11
8403 | 0 | 0 | 0 | 14.2 | 1.11
8404 | 0 | 0 | 0 | 13.9 | 2.22
8405 | 0 | 0 | 0 | 13.8 | 2.22
8406 | 27.8 | 11.1 | 7.3 | 13.6 | 1.11
8407 | 269.4 | 50 | 689.8 | 13.9 | 1.11
8408 | 494.4 | 63.9 | 883.4 | 16.1 | 2.22
8409 | 677.8 | 75 | 959.2 | 20.6 | 4.17
8410 | 788.9 | 86.1 | 953.4 | 22.5 | 3.89
8411 | 850 | 86.1 | 957.8 | 24.2 | 3.89
8412 | 844.4 | 83.3 | 954.3 | 25.3 | 3.33
8413 | 769.4 | 86.1 | 927 | 25.7 | 3.33
8414 | 641.7 | 86.1 | 895.5 | 26.1 | 3.33
8415 | 461.1 | 88.9 | 817.5 | 26.1 | 3.33
8416 | 252.8 | 75 | 689.8 | 25.2 | 3.33
8417 | 44.4 | 22.2 | 7.3 | 23.8 | 2.78
8418 | 0 | 0 | 0 | 20.8 | 2.22
8419 | 0 | 0 | 0 | 19.3 | 1.11
8420 | 0 | 0 | 0 | 18.2 | 1.11
8421 | 0 | 0 | 0 | 17.5 | 1.67
8422 | 0 | 0 | 0 | 16.9 | 1.67
8423 | 0 | 0 | 0 | 16.1 | 2.22
8424 | 0 | 0 | 0 | 15.6 | 5
8425 | 0 | 0 | 0 | 14.6 | 1.94
8426 | 0 | 0 | 0 | 13.6 | 1.67
8427 | 0 | 0 | 0 | 14.2 | 0.83
8428 | 0 | 0 | 0 | 14.2 | 0.83
8429 | 0 | 0 | 0 | 13.5 | 1.67
8430 | 27.8 | 0 | 7.2 | 13.7 | 1.67
8431 | 252.8 | 30.6 | 689.6 | 14.9 | 1.67
8432 | 488.9 | 52.8 | 883.3 | 17.5 | 2.22
8433 | 680.6 | 66.7 | 959.2 | 21.1 | 2.78
8434 | 794.4 | 111.1 | 927.3 | 23.6 | 3.33
8435 | 783.3 | 241.7 | 679.3 | 24.5 | 2.78
8436 | 855.6 | 144.4 | 891.8 | 25 | 2.78
8437 | 777.8 | 88.9 | 934.8 | 25.7 | 2.78
8438 | 644.4 | 77.8 | 913.7 | 25.9 | 3.33
8439 | 469.4 | 75 | 866.6 | 26.2 | 2.78
8440 | 172.2 | 77.8 | 373.3 | 24.7 | 1.11
8441 | 22.2 | 22.2 | 0 | 23.2 | 2.22
8442 | 0 | 0 | 0 | 20.3 | 1.11
8443 | 0 | 0 | 0 | 18.7 | 1.11
8444 | 0 | 0 | 0 | 17.8 | 1.11
8445 | 0 | 0 | 0 | 16.8 | 1.67
8446 | 0 | 0 | 0 | 16 | 1.94
8447 | 0 | 0 | 0 | 15.9 | 2.22
8448 | 0 | 0 | 0 | 15.8 | 5.28
8449 | 0 | 0 | 0 | 15.7 | 0.56
8450 | 0 | 0 | 0 | 15.3 | 1.11
8451 | 0 | 0 | 0 | 15.3 | 1.11
8452 | 0 | 0 | 0 | 14.7 | 1.67
8453 | 0 | 0 | 0 | 14.6 | 1.67
8454 | 13.9 | 0 | 7.1 | 14.6 | 1.11
8455 | 108.3 | 69.4 | 153.8 | 16 | 1.67
8456 | 258.3 | 191.7 | 146.5 | 17 | 2.22
8457 | 558.3 | 305.6 | 407.7 | 21.1 | 3.33
8458 | 619.4 | 266.7 | 478.8 | 23.5 | 5
8459 | 733.3 | 344.4 | 487.8 | 25 | 5
8460 | 397.2 | 408.3 | 0 | 24.2 | 3.89
8461 | 413.9 | 394.4 | 26.4 | 25 | 4.44
8462 | 588.9 | 211.1 | 609.2 | 26.1 | 5
8463 | 325 | 152.8 | 378.5 | 26 | 4.44
8464 | 175 | 94.4 | 318.5 | 25.1 | 4.17
8465 | 25 | 5.6 | 7.1 | 23.3 | 4.17
8466 | 0 | 0 | 0 | 20.9 | 2.78
8467 | 0 | 0 | 0 | 19.7 | 2.22
8468 | 0 | 0 | 0 | 19.3 | 1.94
8469 | 0 | 0 | 0 | 19.5 | 2.78
8470 | 0 | 0 | 0 | 19.5 | 2.78
8471 | 0 | 0 | 0 | 19.4 | 3.33
8472 | 0 | 0 | 0 | 18.7 | 5.56
8473 | 0 | 0 | 0 | 18.5 | 3.61
8474 | 0 | 0 | 0 | 18.5 | 2.78
8475 | 0 | 0 | 0 | 18.1 | 2.78
8476 | 0 | 0 | 0 | 17.5 | 2.78
8477 | 0 | 0 | 0 | 17.6 | 2.78
8478 | 11.1 | 2.8 | 7 | 17.6 | 2.22
8479 | 213.9 | 79.6 | 379 | 17.8 | 1.11
8480 | 458.3 | 63.9 | 867 | 21.5 | 2.22
8481 | 630.6 | 80.6 | 887.1 | 23.2 | 4.17
8482 | 741.7 | 186.2 | 689.9 | 24.8 | 5
8483 | 722.2 | 205.7 | 663.2 | 25.9 | 4.44
8484 | 772.2 | 226.8 | 656.3 | 26.6 | 3.89
8485 | 555.6 | 216.9 | 606.9 | 26.4 | 3.89
8486 | 522.2 | 225 | 479.4 | 26.5 | 3.33
8487 | 366.7 | 152.8 | 470.1 | 26.5 | 2.22
8488 | 161.1 | 77.8 | 329.6 | 25.8 | 3.89
8489 | 25 | 8.3 | 7 | 24.3 | 3.33
8490 | 0 | 0 | 0 | 23.1 | 2.22
8491 | 0 | 0 | 0 | 20.9 | 1.94
8492 | 0 | 0 | 0 | 20.2 | 2.22
8493 | 0 | 0 | 0 | 20 | 2.78
8494 | 0 | 0 | 0 | 19.4 | 2.78
8495 | 0 | 0 | 0 | 19.4 | 4.44
8496 | 0 | 0 | 0 | 19.6 | 5.83
8497 | 0 | 0 | 0 | 19.6 | 3.89
8498 | 0 | 0 | 0 | 19.6 | 3.33
8499 | 0 | 0 | 0 | 19.3 | 2.22
8500 | 0 | 0 | 0 | 19.2 | 3.61
8501 | 0 | 0 | 0 | 19.2 | 3.33
8502 | 2.8 | 10.4 | 8.2 | 19.2 | 2.5
8503 | 83.3 | 97.2 | 0 | 19.6 | 3.33
8504 | 233.3 | 263.9 | 0 | 20.7 | 2.78
8505 | 555.6 | 165.2 | 669.3 | 23.1 | 3.33
8506 | 611.1 | 186.2 | 689.9 | 24.8 | 3.89
8507 | 805.6 | 161.1 | 808.5 | 26.2 | 3.33
8508 | 755.6 | 226.8 | 656.3 | 26.6 | 2.78
8509 | 611.1 | 216.9 | 606.9 | 28.1 | 3.33
8510 | 597.2 | 198.3 | 523.8 | 27.5 | 2.78
8511 | 483.3 | 144 | 489.5 | 27.6 | 2.78
8512 | 194.4 | 66.7 | 505.4 | 26.8 | 3.89
8513 | 30.6 | 13.9 | 7 | 25.6 | 5
8514 | 0 | 0 | 0 | 23.9 | 2.78
8515 | 0 | 0 | 0 | 21.6 | 3.06
8516 | 0 | 0 | 0 | 20.5 | 2.78
8517 | 0 | 0 | 0 | 19.8 | 2.78
8518 | 0 | 0 | 0 | 19.6 | 4.44
8519 | 0 | 0 | 0 | 19.1 | 3.89
8520 | 0 | 0 | 0 | 19.2 | 6.11
8521 | 0 | 0 | 0 | 18.2 | 3.33
8522 | 0 | 0 | 0 | 18.2 | 3.33
8523 | 0 | 0 | 0 | 18.2 | 3.89
8524 | 0 | 0 | 0 | 18.2 | 4.44
8525 | 0 | 0 | 0 | 18.2 | 3.33
8526 | 27.8 | 10.4 | 8.2 | 18.3 | 2.78
8527 | 236.1 | 79.6 | 379 | 18 | 2.78
8528 | 455.6 | 77.8 | 830.3 | 21.4 | 3.89
8529 | 553.6 | 165.2 | 669.3 | 23.1 | 3.89
8530 | 676.9 | 186.2 | 689.9 | 24.6 | 3.89
8531 | 830.6 | 205.7 | 663.2 | 25.5 | 4.44
8532 | 863.9 | 226.8 | 656.3 | 25.2 | 5.28
8533 | 661.1 | 216.9 | 606.9 | 25.4 | 4.44
8534 | 413.9 | 188.9 | 362.9 | 25.7 | 4.44
8535 | 408.3 | 141.7 | 586.1 | 25.6 | 3.89
8536 | 200 | 79.7 | 415.4 | 24.7 | 3.89
8537 | 13.9 | 11.5 | 8.5 | 23.2 | 3.89
8538 | 0 | 0 | 0 | 21.5 | 2.78
8539 | 0 | 0 | 0 | 20.4 | 2.22
8540 | 0 | 0 | 0 | 19.6 | 2.22
8541 | 0 | 0 | 0 | 19.4 | 2.78
8542 | 0 | 0 | 0 | 19.1 | 3.06
8543 | 0 | 0 | 0 | 18.9 | 3.33
8544 | 0 | 0 | 0 | 18.2 | 6.39
8545 | 0 | 0 | 0 | 17.4 | 3.06
8546 | 0 | 0 | 0 | 16.4 | 2.22
8547 | 0 | 0 | 0 | 15.7 | 2.22
8548 | 0 | 0 | 0 | 15.8 | 2.22
8549 | 0 | 0 | 0 | 16 | 2.78
8550 | 8.3 | 10.4 | 8.2 | 16.6 | 2.78
8551 | 180.6 | 79.6 | 379 | 18 | 2.5
8552 | 452.8 | 94.4 | 787.4 | 21.5 | 2.78
8553 | 627.8 | 97.2 | 855.5 | 21.8 | 4.44
8554 | 725 | 141.7 | 791.7 | 24 | 4.44
8555 | 697.2 | 261.1 | 547 | 25.1 | 3.89
8556 | 686.1 | 226.8 | 656.3 | 25.5 | 3.33
8557 | 633.3 | 216.9 | 606.9 | 27.3 | 2.78
8558 | 600 | 211.1 | 627.1 | 27.1 | 2.78
8559 | 411.1 | 144 | 489.5 | 26 | 2.78
8560 | 227.8 | 66.7 | 636.9 | 25.8 | 2.78
8561 | 27.8 | 5.6 | 7.1 | 23 | 3.06
8562 | 0 | 0 | 0 | 20.9 | 2.78
8563 | 0 | 0 | 0 | 19.5 | 2.22
8564 | 0 | 0 | 0 | 19.1 | 2.22
8565 | 0 | 0 | 0 | 18.9 | 3.06
8566 | 0 | 0 | 0 | 18.2 | 4.72
8567 | 0 | 0 | 0 | 17.6 | 4.17
8568 | 0 | 0 | 0 | 16.7 | 6.67
8569 | 0 | 0 | 0 | 16.2 | 3.33
8570 | 0 | 0 | 0 | 16.3 | 3.33
8571 | 0 | 0 | 0 | 16.7 | 3.33
8572 | 0 | 0 | 0 | 15.9 | 3.33
8573 | 0 | 0 | 0 | 15.5 | 2.78
8574 | 19.4 | 2.8 | 7.2 | 15.2 | 2.78
8575 | 152.8 | 91.7 | 241.5 | 16.4 | 3.33
8576 | 416.7 | 119.4 | 652.9 | 17.2 | 3.89
8577 | 613.9 | 161.1 | 729.9 | 19.5 | 3.89
8578 | 722.2 | 200 | 708.5 | 22.6 | 3.33
8579 | 750 | 205.7 | 663.2 | 24.2 | 3.33
8580 | 766.7 | 226.8 | 656.3 | 25.6 | 2.78
8581 | 638.9 | 216.9 | 606.9 | 26.8 | 2.78
8582 | 441.7 | 302.8 | 223.9 | 27.3 | 2.22
8583 | 288.9 | 230.6 | 128.1 | 26.8 | 2.22
8584 | 108.3 | 79.7 | 415.4 | 25.3 | 1.67
8585 | 19.4 | 16.7 | 7.2 | 23.3 | 2.22
8586 | 0 | 0 | 0 | 21.6 | 2.78
8587 | 0 | 0 | 0 | 20.2 | 3.06
8588 | 0 | 0 | 0 | 19.3 | 2.78
8589 | 0 | 0 | 0 | 19 | 2.78
8590 | 0 | 0 | 0 | 18.5 | 3.89
8591 | 0 | 0 | 0 | 18.2 | 2.78
8592 | 0 | 0 | 0 | 18.1 | 6.94
8593 | 0 | 0 | 0 | 18.1 | 2.22
8594 | 0 | 0 | 0 | 17.8 | 2.78
8595 | 0 | 0 | 0 | 17.5 | 2.22
8596 | 0 | 0 | 0 | 17.3 | 3.33
8597 | 0 | 0 | 0 | 17.3 | 2.78
8598 | 16.7 | 27.8 | 0 | 17.2 | 2.22
8599 | 191.7 | 79.6 | 379 | 17.5 | 2.78
8600 | 358.3 | 136.8 | 612.9 | 18.6 | 3.33
8601 | 566.7 | 197.2 | 595.4 | 21.8 | 3.89
8602 | 750 | 261.1 | 663.1 | 23.4 | 4.44
8603 | 608.3 | 425 | 229.8 | 24.4 | 3.89
8604 | 694.4 | 438.9 | 320.4 | 24.9 | 2.78
8605 | 633.3 | 366.7 | 361.7 | 25.9 | 3.33
8606 | 422.2 | 288.9 | 214.9 | 25.9 | 3.89
8607 | 277.8 | 172.2 | 231.8 | 23.4 | 4.44
8608 | 111.1 | 91.7 | 76.8 | 22.9 | 3.33
8609 | 16.7 | 11.1 | 7.4 | 22.4 | 2.78
8610 | 0 | 0 | 0 | 20.9 | 2.22
8611 | 0 | 0 | 0 | 19.9 | 2.22
8612 | 0 | 0 | 0 | 19.8 | 2.78
8613 | 0 | 0 | 0 | 18.9 | 2.78
8614 | 0 | 0 | 0 | 18.6 | 2.78
8615 | 0 | 0 | 0 | 18.6 | 3.33
8616 | 0 | 0 | 0 | 18.9 | 7.22
8617 | 0 | 0 | 0 | 18.9 | 2.78
8618 | 0 | 0 | 0 | 18.9 | 2.78
8619 | 0 | 0 | 0 | 18.5 | 2.78
8620 | 0 | 0 | 0 | 17.6 | 2.22
8621 | 0 | 0 | 0 | 17.9 | 2.22
8622 | 5.6 | 10.4 | 8.2 | 17.9 | 2.22
8623 | 91.7 | 97.2 | 0 | 17.9 | 2.78
8624 | 163.9 | 183.3 | 0 | 18.7 | 5
8625 | 461.1 | 191.7 | 434 | 22.1 | 5.56
8626 | 736.1 | 113.9 | 843.6 | 24.4 | 5
8627 | 794.4 | 119.4 | 845.8 | 27 | 5
8628 | 736.1 | 288.9 | 560.4 | 26.4 | 3.89
8629 | 494.4 | 216.9 | 606.9 | 25.4 | 3.33
8630 | 538.9 | 216.7 | 519 | 26.8 | 3.89
8631 | 300 | 213.9 | 189 | 25.3 | 3.89
8632 | 125 | 111.1 | 54.8 | 23.8 | 4.44
8633 | 22.2 | 19.4 | 7.6 | 22.4 | 5
8634 | 0 | 0 | 0 | 21.4 | 3.89
8635 | 0 | 0 | 0 | 21.1 | 2.78
8636 | 0 | 0 | 0 | 20.9 | 3.89
8637 | 0 | 0 | 0 | 20.2 | 4.72
8638 | 0 | 0 | 0 | 19.4 | 3.33
8639 | 0 | 0 | 0 | 19.2 | 3.33
8640 | 0 | 0 | 0 | 18.8 | 7.5
8641 | 0 | 0 | 0 | 18.6 | 3.33
8642 | 0 | 0 | 0 | 18.3 | 2.78
8643 | 0 | 0 | 0 | 18.1 | 1.67
8644 | 0 | 0 | 0 | 18 | 3.89
8645 | 0 | 0 | 0 | 17.6 | 2.78
8646 | 13.9 | 5.6 | 7.8 | 17.9 | 2.78
8647 | 205.6 | 108.3 | 383.3 | 18.8 | 2.78
8648 | 227.8 | 216.7 | 24.4 | 21.6 | 4.44
8649 | 405.6 | 294.4 | 178.9 | 22.2 | 5.56
8650 | 588.9 | 375 | 289.8 | 23 | 5
8651 | 550 | 477.8 | 90.5 | 24.4 | 5.56
8652 | 300 | 319.4 | 0 | 23.4 | 6.11
8653 | 150 | 163.9 | 0 | 23.9 | 4.44
8654 | 188.9 | 191.7 | 0 | 23.4 | 3.89
8655 | 69.4 | 69.4 | 0 | 23.5 | 2.78
8656 | 52.8 | 41.7 | 43.8 | 22.7 | 2.78
8657 | 8.3 | 2.8 | 7.8 | 20.7 | 2.78
8658 | 0 | 0 | 0 | 19.5 | 4.44
8659 | 0 | 0 | 0 | 19.5 | 1.67
8660 | 0 | 0 | 0 | 19.1 | 1.11
8661 | 0 | 0 | 0 | 17.3 | 1.94
8662 | 0 | 0 | 0 | 17.4 | 2.78
8663 | 0 | 0 | 0 | 17 | 1.67
8664 | 0 | 0 | 0 | 17.1 | 7.78
8665 | 0 | 0 | 0 | 17.1 | 2.78
8666 | 0 | 0 | 0 | 16.8 | 2.78
8667 | 0 | 0 | 0 | 16.9 | 2.22
8668 | 0 | 0 | 0 | 17 | 1.67
8669 | 0 | 0 | 0 | 17.2 | 2.22
8670 | 8.3 | 25 | 0 | 17.2 | 1.11
8671 | 166.7 | 144.4 | 87.5 | 17.7 | 1.67
8672 | 313.9 | 280.6 | 73 | 18.9 | 1.67
8673 | 463.9 | 352.8 | 178.7 | 21.7 | 2.78
8674 | 633.3 | 288.9 | 466.4 | 23.4 | 2.22
8675 | 791.7 | 250 | 678 | 24.7 | 3.89
8676 | 694.4 | 327.8 | 458.9 | 25.5 | 3.89
8677 | 533.3 | 316.7 | 293.4 | 24.5 | 2.78
8678 | 319.4 | 269.4 | 80.4 | 24.3 | 2.78
8679 | 375 | 202.8 | 377.4 | 24.1 | 2.78
8680 | 200 | 108.3 | 360.9 | 22.9 | 2.78
8681 | 27.8 | 11.1 | 8.1 | 21.8 | 2.22
8682 | 0 | 0 | 0 | 21 | 1.67
8683 | 0 | 0 | 0 | 20.3 | 1.67
8684 | 0 | 0 | 0 | 19.6 | 1.67
8685 | 0 | 0 | 0 | 19 | 2.22
8686 | 0 | 0 | 0 | 19.1 | 1.11
8687 | 0 | 0 | 0 | 19.1 | 1.67
8688 | 0 | 0 | 0 | 18.2 | 8.06
8689 | 0 | 0 | 0 | 17.8 | 2.38
8690 | 0 | 0 | 0 | 17.9 | 2.36
8691 | 0 | 0 | 0 | 18 | 2.27
8692 | 0 | 0 | 0 | 18.1 | 2.38
8693 | 0 | 0 | 0 | 18.1 | 2.39
8694 | 8.3 | 5.6 | 8.5 | 18.2 | 2.18
8695 | 122.2 | 88.9 | 131.1 | 18.5 | 2.07
8696 | 397.2 | 116.7 | 614.2 | 19.7 | 2.91
8697 | 483.3 | 252.8 | 370.6 | 21.5 | 3.41
8698 | 663.9 | 280.6 | 518.7 | 24 | 3.63
8699 | 608.3 | 286.1 | 403 | 25 | 3.72
8700 | 780.6 | 280.6 | 625.4 | 24.8 | 3.54
8701 | 613.9 | 183.3 | 582.6 | 24.9 | 3.18
8702 | 497.2 | 175 | 518 | 25.3 | 3.14
8703 | 450 | 127.8 | 705.4 | 25.7 | 2.93
8704 | 188.9 | 75 | 447.9 | 25.1 | 2.98
8705 | 11.1 | 11.1 | 0 | 23.6 | 2.94
8706 | 0 | 0 | 0 | 22.1 | 2.37
8707 | 0 | 0 | 0 | 21 | 2.04
8708 | 0 | 0 | 0 | 20.2 | 2.15
8709 | 0 | 0 | 0 | 18.8 | 2.45
8710 | 0 | 0 | 0 | 18.2 | 2.54
8711 | 0 | 0 | 0 | 18 | 2.6
8712 | 0 | 0 | 0 | 17.8 | 8.33
8713 | 0 | 0 | 0 | 17.7 | 3.89
8714 | 0 | 0 | 0 | 17.5 | 4.44
8715 | 0 | 0 | 0 | 17.7 | 2.78
8716 | 0 | 0 | 0 | 17.7 | 2.78
8717 | 0 | 0 | 0 | 17 | 2.22
8718 | 19.4 | 8.3 | 8.9 | 16.5 | 1.67
8719 | 205.6 | 75 | 512.7 | 17.1 | 1.67
8720 | 427.8 | 111.1 | 692.6 | 20.5 | 3.33
8721 | 616.7 | 102.8 | 825.3 | 22 | 3.89
8722 | 738.9 | 111.1 | 848.8 | 24.2 | 2.78
8723 | 783.3 | 150 | 791.5 | 25.5 | 2.22
8724 | 772.2 | 213.9 | 697.8 | 26.4 | 2.22
8725 | 683.3 | 294.4 | 525.8 | 26.7 | 2.22
8726 | 586.1 | 225 | 580 | 27 | 1.11
8727 | 330.6 | 141.7 | 413.1 | 26.7 | 1.11
8728 | 197.2 | 102.8 | 370.9 | 26 | 1.11
8729 | 22.2 | 19.4 | 8.9 | 24.4 | 1.39
8730 | 0 | 0 | 0 | 22.9 | 1.11
8731 | 0 | 0 | 0 | 21.7 | 1.11
8732 | 0 | 0 | 0 | 20.5 | 1.11
8733 | 0 | 0 | 0 | 19.7 | 1.11
8734 | 0 | 0 | 0 | 18.9 | 2.78
8735 | 0 | 0 | 0 | 18.3 | 2.78
8736 | 0 | 0 | 0 | 18.5 | 8.61
8737 | 0 | 0 | 0 | 18.5 | 2.78
8738 | 0 | 0 | 0 | 18.1 | 2.78
8739 | 0 | 0 | 0 | 17.2 | 2.78
8740 | 0 | 0 | 0 | 16.8 | 2.22
8741 | 0 | 0 | 0 | 16.8 | 2.22
8742 | 22.2 | 11.1 | 9.4 | 16.7 | 2.78
8743 | 200 | 80.6 | 468.3 | 17.9 | 2.22
8744 | 419.4 | 147.2 | 594.7 | 19.8 | 2.78
8745 | 613.9 | 150 | 744.3 | 22.2 | 2.5
8746 | 738.9 | 141.7 | 806.8 | 24.4 | 2.78
8747 | 625 | 200 | 530.7 | 25.3 | 2.78
8748 | 630.6 | 297.2 | 416.2 | 25.1 | 2.22
8749 | 558.3 | 280.6 | 375.3 | 26.4 | 1.11
8750 | 377.8 | 241.7 | 218.4 | 25.3 | 1.67
8751 | 275 | 186.1 | 194.2 | 25.7 | 0.83
8752 | 200 | 105.6 | 370.3 | 25.2 | 1.94
8753 | 11.1 | 13.9 | 0 | 23.5 | 1.11
8754 | 0 | 0 | 0 | 22.3 | 1.67
8755 | 0 | 0 | 0 | 21.3 | 1.67
8756 | 0 | 0 | 0 | 20 | 1.67
8757 | 0 | 0 | 0 | 19 | 1.67
8758 | 0 | 0 | 0 | 18.1 | 1.11
8759 | 0 | 0 | 0 | 17.2 | 1.67
Note on B1: Author: (W/sq.m)
Note on C1: Author: (W/Sq.m)
Note on D1: Author: (W/Sq.m)
Note on E1: Author: (°C)
Note on F1: Author: (m/s)